## Summary
BASELOAD PPA ANALYSIS: Solar + Wind + BESS
Zone: SE3 ¦ Year: 2024 ¦ Profile: south_lundby + ENTSO-E wind
INPUT PARAMETERS
Solar Capacity (MW) | 1
Wind Capacity (MW) | 1
Baseload Target (%) | 0.8
BESS Round-Trip Efficiency | 0.9
BESS Initial SoC (%) | 0.5
CALCULATED PARAMETERS
Solar Capacity Factor |  | 0.1152
Wind Capacity Factor |  | 0.3000
Combined Capacity Factor |  | 0.2076
Mean Production (MW) |  | 0.4152
Total Hours |  | 8784
Annual Production (MWh) |  | 3647.2
KEY RESULTS
Baseload Level (MW)
BESS Capacity Required (MWh)
BESS Power Required (MW)
Deficit Hours
Surplus Hours
Deficit Hours %

## Hourly
Timestamp | Month | Day | Hour | Solar CF | Wind CF | Solar (MW) | Wind (MW) | Deficit (MW) | Surplus (MW) | BESS Flow (MW) | BESS SoC (MWh) | Total (MW) | Baseload (MW) | Net (MW)
2024-01-01 | 1 | 1 | 0 | 0% | 47%
2024-01-01 01:00 | 1 | 1 | 1 | 0% | 44.09%
2024-01-01 02:00 | 1 | 1 | 2 | 0% | 43.09%
2024-01-01 03:00 | 1 | 1 | 3 | 0% | 41.97%
2024-01-01 04:00 | 1 | 1 | 4 | 0% | 41.03%
2024-01-01 05:00 | 1 | 1 | 5 | 0% | 40.38%
2024-01-01 06:00 | 1 | 1 | 6 | 0% | 39.84%
2024-01-01 07:00 | 1 | 1 | 7 | 0% | 39.05%
2024-01-01 08:00 | 1 | 1 | 8 | 0% | 38.37%
2024-01-01 09:00 | 1 | 1 | 9 | 3.088% | 37.95%
2024-01-01 10:00 | 1 | 1 | 10 | 11.97% | 37.49%
2024-01-01 11:00 | 1 | 1 | 11 | 18.08% | 36.51%
2024-01-01 12:00 | 1 | 1 | 12 | 19.67% | 35.35%
2024-01-01 13:00 | 1 | 1 | 13 | 15.2% | 36.91%
2024-01-01 14:00 | 1 | 1 | 14 | 7.187% | 35.83%
2024-01-01 15:00 | 1 | 1 | 15 | 0% | 37.36%
2024-01-01 16:00 | 1 | 1 | 16 | 0% | 38.68%
2024-01-01 17:00 | 1 | 1 | 17 | 0% | 40.31%
2024-01-01 18:00 | 1 | 1 | 18 | 0% | 42.24%
2024-01-01 19:00 | 1 | 1 | 19 | 0% | 43.71%
2024-01-01 20:00 | 1 | 1 | 20 | 0% | 41.87%
2024-01-01 21:00 | 1 | 1 | 21 | 0% | 46.63%
2024-01-01 22:00 | 1 | 1 | 22 | 0% | 47.18%
2024-01-01 23:00 | 1 | 1 | 23 | 0% | 47.62%
2024-01-02 | 1 | 2 | 0 | 0% | 39.03%
2024-01-02 01:00 | 1 | 2 | 1 | 0% | 46.4%
2024-01-02 02:00 | 1 | 2 | 2 | 0% | 45.88%
2024-01-02 03:00 | 1 | 2 | 3 | 0% | 46.37%
2024-01-02 04:00 | 1 | 2 | 4 | 0% | 44.87%
2024-01-02 05:00 | 1 | 2 | 5 | 0% | 44.71%
2024-01-02 06:00 | 1 | 2 | 6 | 0% | 44.77%
2024-01-02 07:00 | 1 | 2 | 7 | 0% | 44.31%
2024-01-02 08:00 | 1 | 2 | 8 | 0% | 44.04%
2024-01-02 09:00 | 1 | 2 | 9 | 3.274% | 43.78%
2024-01-02 10:00 | 1 | 2 | 10 | 12.42% | 42.92%
2024-01-02 11:00 | 1 | 2 | 11 | 18.84% | 41.58%
2024-01-02 12:00 | 1 | 2 | 12 | 20.45% | 40.58%
2024-01-02 13:00 | 1 | 2 | 13 | 15.96% | 40.16%
2024-01-02 14:00 | 1 | 2 | 14 | 7.812% | 40.17%
2024-01-02 15:00 | 1 | 2 | 15 | 0% | 41.04%
2024-01-02 16:00 | 1 | 2 | 16 | 0% | 41.36%
2024-01-02 17:00 | 1 | 2 | 17 | 0% | 41.23%
2024-01-02 18:00 | 1 | 2 | 18 | 0% | 41.19%
2024-01-02 19:00 | 1 | 2 | 19 | 0% | 40.98%
2024-01-02 20:00 | 1 | 2 | 20 | 0% | 40.56%
2024-01-02 21:00 | 1 | 2 | 21 | 0% | 40.3%
2024-01-02 22:00 | 1 | 2 | 22 | 0% | 39.72%
2024-01-02 23:00 | 1 | 2 | 23 | 0% | 42.64%
2024-01-03 | 1 | 3 | 0 | 0% | 48.58%
2024-01-03 01:00 | 1 | 3 | 1 | 0% | 38.97%
2024-01-03 02:00 | 1 | 3 | 2 | 0% | 38.45%
2024-01-03 03:00 | 1 | 3 | 3 | 0% | 38.22%
2024-01-03 04:00 | 1 | 3 | 4 | 0% | 38.11%
2024-01-03 05:00 | 1 | 3 | 5 | 0% | 38.05%
2024-01-03 06:00 | 1 | 3 | 6 | 0% | 38.04%
2024-01-03 07:00 | 1 | 3 | 7 | 0% | 38.27%
2024-01-03 08:00 | 1 | 3 | 8 | 0% | 37.35%
2024-01-03 09:00 | 1 | 3 | 9 | 0.8834% | 37.48%
2024-01-03 10:00 | 1 | 3 | 10 | 0.8684% | 38.09%
2024-01-03 11:00 | 1 | 3 | 11 | 1.344% | 38.61%
2024-01-03 12:00 | 1 | 3 | 12 | 5.815% | 42.72%
2024-01-03 13:00 | 1 | 3 | 13 | 11.72% | 40.88%
2024-01-03 14:00 | 1 | 3 | 14 | 5.452% | 42.36%
2024-01-03 15:00 | 1 | 3 | 15 | 0% | 44.42%
2024-01-03 16:00 | 1 | 3 | 16 | 0% | 45.92%
2024-01-03 17:00 | 1 | 3 | 17 | 0% | 46.6%
2024-01-03 18:00 | 1 | 3 | 18 | 0% | 48.17%
2024-01-03 19:00 | 1 | 3 | 19 | 0% | 48.72%
2024-01-03 20:00 | 1 | 3 | 20 | 0% | 49.1%
2024-01-03 21:00 | 1 | 3 | 21 | 0% | 48.84%
2024-01-03 22:00 | 1 | 3 | 22 | 0% | 48.72%
2024-01-03 23:00 | 1 | 3 | 23 | 0% | 47.94%
2024-01-04 | 1 | 4 | 0 | 0% | 37.58%
2024-01-04 01:00 | 1 | 4 | 1 | 0% | 49.44%
2024-01-04 02:00 | 1 | 4 | 2 | 0% | 50.21%
2024-01-04 03:00 | 1 | 4 | 3 | 0% | 51.23%
2024-01-04 04:00 | 1 | 4 | 4 | 0% | 51.71%
2024-01-04 05:00 | 1 | 4 | 5 | 0% | 52.4%
2024-01-04 06:00 | 1 | 4 | 6 | 0% | 52.6%
2024-01-04 07:00 | 1 | 4 | 7 | 0% | 52.51%
2024-01-04 08:00 | 1 | 4 | 8 | 0% | 52.32%
2024-01-04 09:00 | 1 | 4 | 9 | 2.515% | 51.61%
2024-01-04 10:00 | 1 | 4 | 10 | 12.7% | 51.56%
2024-01-04 11:00 | 1 | 4 | 11 | 19.18% | 50.69%
2024-01-04 12:00 | 1 | 4 | 12 | 20.89% | 49.57%
2024-01-04 13:00 | 1 | 4 | 13 | 16.51% | 48.52%
2024-01-04 14:00 | 1 | 4 | 14 | 5.894% | 48.21%
2024-01-04 15:00 | 1 | 4 | 15 | 0% | 48.35%
2024-01-04 16:00 | 1 | 4 | 16 | 0% | 48.06%
2024-01-04 17:00 | 1 | 4 | 17 | 0% | 47.49%
2024-01-04 18:00 | 1 | 4 | 18 | 0% | 46.05%
2024-01-04 19:00 | 1 | 4 | 19 | 0% | 44.37%
2024-01-04 20:00 | 1 | 4 | 20 | 0% | 42.29%
2024-01-04 21:00 | 1 | 4 | 21 | 0% | 40.81%
2024-01-04 22:00 | 1 | 4 | 22 | 0% | 39.45%
2024-01-04 23:00 | 1 | 4 | 23 | 0% | 38.42%
2024-01-05 | 1 | 5 | 0 | 0% | 27.83%
2024-01-05 01:00 | 1 | 5 | 1 | 0% | 38.54%
2024-01-05 02:00 | 1 | 5 | 2 | 0% | 35.24%
2024-01-05 03:00 | 1 | 5 | 3 | 0% | 33.94%
2024-01-05 04:00 | 1 | 5 | 4 | 0% | 34.82%
2024-01-05 05:00 | 1 | 5 | 5 | 0% | 31.65%
2024-01-05 06:00 | 1 | 5 | 6 | 0% | 31.46%
2024-01-05 07:00 | 1 | 5 | 7 | 0% | 30.09%
2024-01-05 08:00 | 1 | 5 | 8 | 0% | 27.34%
2024-01-05 09:00 | 1 | 5 | 9 | 3.836% | 26.05%
2024-01-05 10:00 | 1 | 5 | 10 | 13.36% | 23.94%
2024-01-05 11:00 | 1 | 5 | 11 | 19.98% | 22.41%
2024-01-05 12:00 | 1 | 5 | 12 | 21.52% | 22.08%
2024-01-05 13:00 | 1 | 5 | 13 | 17.15% | 21.94%
2024-01-05 14:00 | 1 | 5 | 14 | 8.701% | 22.04%
2024-01-05 15:00 | 1 | 5 | 15 | 0% | 22.98%
2024-01-05 16:00 | 1 | 5 | 16 | 0% | 23.61%
2024-01-05 17:00 | 1 | 5 | 17 | 0% | 23.82%
2024-01-05 18:00 | 1 | 5 | 18 | 0% | 24.52%
2024-01-05 19:00 | 1 | 5 | 19 | 0% | 24.9%
2024-01-05 20:00 | 1 | 5 | 20 | 0% | 25.11%
2024-01-05 21:00 | 1 | 5 | 21 | 0% | 25.77%
2024-01-05 22:00 | 1 | 5 | 22 | 0% | 26.34%
2024-01-05 23:00 | 1 | 5 | 23 | 0% | 27.07%
2024-01-06 | 1 | 6 | 0 | 0% | 42.38%
2024-01-06 01:00 | 1 | 6 | 1 | 0% | 29.73%
2024-01-06 02:00 | 1 | 6 | 2 | 0% | 28.63%
2024-01-06 03:00 | 1 | 6 | 3 | 0% | 29.66%
2024-01-06 04:00 | 1 | 6 | 4 | 0% | 32.98%
2024-01-06 05:00 | 1 | 6 | 5 | 0% | 31.74%
2024-01-06 06:00 | 1 | 6 | 6 | 0% | 33.16%
2024-01-06 07:00 | 1 | 6 | 7 | 0% | 34.34%
2024-01-06 08:00 | 1 | 6 | 8 | 0% | 35.76%
2024-01-06 09:00 | 1 | 6 | 9 | 0.8235% | 36.71%
2024-01-06 10:00 | 1 | 6 | 10 | 4.43% | 37.16%
2024-01-06 11:00 | 1 | 6 | 11 | 5.541% | 36.87%
2024-01-06 12:00 | 1 | 6 | 12 | 5.776% | 36.67%
2024-01-06 13:00 | 1 | 6 | 13 | 3.865% | 36.91%
2024-01-06 14:00 | 1 | 6 | 14 | 1.662% | 37.95%
2024-01-06 15:00 | 1 | 6 | 15 | 0% | 39.83%
2024-01-06 16:00 | 1 | 6 | 16 | 0% | 41.05%
2024-01-06 17:00 | 1 | 6 | 17 | 0% | 42.04%
2024-01-06 18:00 | 1 | 6 | 18 | 0% | 42.52%
2024-01-06 19:00 | 1 | 6 | 19 | 0% | 43%
2024-01-06 20:00 | 1 | 6 | 20 | 0% | 42.96%
2024-01-06 21:00 | 1 | 6 | 21 | 0% | 43.05%
2024-01-06 22:00 | 1 | 6 | 22 | 0% | 43.09%
2024-01-06 23:00 | 1 | 6 | 23 | 0% | 42.78%
2024-01-07 | 1 | 7 | 0 | 0% | 41.52%
2024-01-07 01:00 | 1 | 7 | 1 | 0% | 41.74%
2024-01-07 02:00 | 1 | 7 | 2 | 0% | 40.67%
2024-01-07 03:00 | 1 | 7 | 3 | 0% | 38.68%
2024-01-07 04:00 | 1 | 7 | 4 | 0% | 37.25%
2024-01-07 05:00 | 1 | 7 | 5 | 0% | 35.39%
2024-01-07 06:00 | 1 | 7 | 6 | 0% | 34.19%
2024-01-07 07:00 | 1 | 7 | 7 | 0% | 33.01%
2024-01-07 08:00 | 1 | 7 | 8 | 0% | 31.79%
2024-01-07 09:00 | 1 | 7 | 9 | 3.344% | 31.71%
2024-01-07 10:00 | 1 | 7 | 10 | 12.73% | 32.01%
2024-01-07 11:00 | 1 | 7 | 11 | 19.69% | 32.33%
2024-01-07 12:00 | 1 | 7 | 12 | 21.08% | 32.52%
2024-01-07 13:00 | 1 | 7 | 13 | 16.91% | 33.36%
2024-01-07 14:00 | 1 | 7 | 14 | 8.441% | 34.25%
2024-01-07 15:00 | 1 | 7 | 15 | 0% | 36.42%
2024-01-07 16:00 | 1 | 7 | 16 | 0% | 38.36%
2024-01-07 17:00 | 1 | 7 | 17 | 0% | 40.2%
2024-01-07 18:00 | 1 | 7 | 18 | 0% | 41.23%
2024-01-07 19:00 | 1 | 7 | 19 | 0% | 42.49%
2024-01-07 20:00 | 1 | 7 | 20 | 0% | 42.82%
2024-01-07 21:00 | 1 | 7 | 21 | 0% | 42.64%
2024-01-07 22:00 | 1 | 7 | 22 | 0% | 41.7%
2024-01-07 23:00 | 1 | 7 | 23 | 0% | 41.23%
2024-01-08 | 1 | 8 | 0 | 0% | 33.64%
2024-01-08 01:00 | 1 | 8 | 1 | 0% | 40.95%
2024-01-08 02:00 | 1 | 8 | 2 | 0% | 40.72%
2024-01-08 03:00 | 1 | 8 | 3 | 0% | 40.22%
2024-01-08 04:00 | 1 | 8 | 4 | 0% | 40.12%
2024-01-08 05:00 | 1 | 8 | 5 | 0% | 40.45%
2024-01-08 06:00 | 1 | 8 | 6 | 0% | 41.05%
2024-01-08 07:00 | 1 | 8 | 7 | 0% | 41.88%
2024-01-08 08:00 | 1 | 8 | 8 | 0% | 42.02%
2024-01-08 09:00 | 1 | 8 | 9 | 0% | 41.77%
2024-01-08 10:00 | 1 | 8 | 10 | 0.2463% | 41.02%
2024-01-08 11:00 | 1 | 8 | 11 | 1.351% | 39.92%
2024-01-08 12:00 | 1 | 8 | 12 | 0.778% | 38.66%
2024-01-08 13:00 | 1 | 8 | 13 | 0.3217% | 37.92%
2024-01-08 14:00 | 1 | 8 | 14 | 0% | 37.72%
2024-01-08 15:00 | 1 | 8 | 15 | 0% | 37.74%
2024-01-08 16:00 | 1 | 8 | 16 | 0% | 37.7%
2024-01-08 17:00 | 1 | 8 | 17 | 0% | 37.24%
2024-01-08 18:00 | 1 | 8 | 18 | 0% | 36.98%
2024-01-08 19:00 | 1 | 8 | 19 | 0% | 36.24%
2024-01-08 20:00 | 1 | 8 | 20 | 0% | 35.44%
2024-01-08 21:00 | 1 | 8 | 21 | 0% | 34.49%
2024-01-08 22:00 | 1 | 8 | 22 | 0% | 33.79%
2024-01-08 23:00 | 1 | 8 | 23 | 0% | 33.78%
2024-01-09 | 1 | 9 | 0 | 0% | 30.65%
2024-01-09 01:00 | 1 | 9 | 1 | 0% | 33.32%
2024-01-09 02:00 | 1 | 9 | 2 | 0% | 33.14%
2024-01-09 03:00 | 1 | 9 | 3 | 0% | 32.96%
2024-01-09 04:00 | 1 | 9 | 4 | 0% | 32.82%
2024-01-09 05:00 | 1 | 9 | 5 | 0% | 32.35%
2024-01-09 06:00 | 1 | 9 | 6 | 0% | 31.94%
2024-01-09 07:00 | 1 | 9 | 7 | 0% | 31.12%
2024-01-09 08:00 | 1 | 9 | 8 | 0% | 30.3%
2024-01-09 09:00 | 1 | 9 | 9 | 1.324% | 29.11%
2024-01-09 10:00 | 1 | 9 | 10 | 3.69% | 27.59%
2024-01-09 11:00 | 1 | 9 | 11 | 6.09% | 26.02%
2024-01-09 12:00 | 1 | 9 | 12 | 6.543% | 24.89%
2024-01-09 13:00 | 1 | 9 | 13 | 4.504% | 24.39%
2024-01-09 14:00 | 1 | 9 | 14 | 3.544% | 24.48%
2024-01-09 15:00 | 1 | 9 | 15 | 0.1967% | 25.16%
2024-01-09 16:00 | 1 | 9 | 16 | 0% | 25.67%
2024-01-09 17:00 | 1 | 9 | 17 | 0% | 26.58%
2024-01-09 18:00 | 1 | 9 | 18 | 0% | 27.93%
2024-01-09 19:00 | 1 | 9 | 19 | 0% | 28.31%
2024-01-09 20:00 | 1 | 9 | 20 | 0% | 29.05%
2024-01-09 21:00 | 1 | 9 | 21 | 0% | 29.7%
2024-01-09 22:00 | 1 | 9 | 22 | 0% | 30.99%
2024-01-09 23:00 | 1 | 9 | 23 | 0% | 31.63%
2024-01-10 | 1 | 10 | 0 | 0% | 49.31%
2024-01-10 01:00 | 1 | 10 | 1 | 0% | 30.61%
2024-01-10 02:00 | 1 | 10 | 2 | 0% | 30.6%
2024-01-10 03:00 | 1 | 10 | 3 | 0% | 30.71%
2024-01-10 04:00 | 1 | 10 | 4 | 0% | 31.22%
2024-01-10 05:00 | 1 | 10 | 5 | 0% | 31.54%
2024-01-10 06:00 | 1 | 10 | 6 | 0% | 32.34%
2024-01-10 07:00 | 1 | 10 | 7 | 0% | 32.78%
2024-01-10 08:00 | 1 | 10 | 8 | 0% | 33.36%
2024-01-10 09:00 | 1 | 10 | 9 | 2.02% | 34.28%
2024-01-10 10:00 | 1 | 10 | 10 | 0.2421% | 35.12%
2024-01-10 11:00 | 1 | 10 | 11 | 0.8508% | 35.22%
2024-01-10 12:00 | 1 | 10 | 12 | 0.9289% | 35.66%
2024-01-10 13:00 | 1 | 10 | 13 | 1.093% | 36.63%
2024-01-10 14:00 | 1 | 10 | 14 | 1.077% | 38.32%
2024-01-10 15:00 | 1 | 10 | 15 | 0% | 40.22%
2024-01-10 16:00 | 1 | 10 | 16 | 0% | 42.37%
2024-01-10 17:00 | 1 | 10 | 17 | 0% | 43.59%
2024-01-10 18:00 | 1 | 10 | 18 | 0% | 44.07%
2024-01-10 19:00 | 1 | 10 | 19 | 0% | 44.32%
2024-01-10 20:00 | 1 | 10 | 20 | 0% | 44.71%
2024-01-10 21:00 | 1 | 10 | 21 | 0% | 45.91%
2024-01-10 22:00 | 1 | 10 | 22 | 0% | 46.76%
2024-01-10 23:00 | 1 | 10 | 23 | 0% | 47.76%
2024-01-11 | 1 | 11 | 0 | 0% | 46.06%
2024-01-11 01:00 | 1 | 11 | 1 | 0% | 51.02%
2024-01-11 02:00 | 1 | 11 | 2 | 0% | 52.04%
2024-01-11 03:00 | 1 | 11 | 3 | 0% | 53.29%
2024-01-11 04:00 | 1 | 11 | 4 | 0% | 54.21%
2024-01-11 05:00 | 1 | 11 | 5 | 0% | 54.7%
2024-01-11 06:00 | 1 | 11 | 6 | 0% | 54.93%
2024-01-11 07:00 | 1 | 11 | 7 | 0% | 55.24%
2024-01-11 08:00 | 1 | 11 | 8 | 0% | 55.36%
2024-01-11 09:00 | 1 | 11 | 9 | 0.3171% | 55.1%
2024-01-11 10:00 | 1 | 11 | 10 | 2.729% | 54.74%
2024-01-11 11:00 | 1 | 11 | 11 | 1.515% | 54.39%
2024-01-11 12:00 | 1 | 11 | 12 | 0.7041% | 52.84%
2024-01-11 13:00 | 1 | 11 | 13 | 1.016% | 52.15%
2024-01-11 14:00 | 1 | 11 | 14 | 1.074% | 51.88%
2024-01-11 15:00 | 1 | 11 | 15 | 0% | 51.65%
2024-01-11 16:00 | 1 | 11 | 16 | 0% | 50.97%
2024-01-11 17:00 | 1 | 11 | 17 | 0% | 50.32%
2024-01-11 18:00 | 1 | 11 | 18 | 0% | 48.74%
2024-01-11 19:00 | 1 | 11 | 19 | 0% | 45.81%
2024-01-11 20:00 | 1 | 11 | 20 | 0% | 48.46%
2024-01-11 21:00 | 1 | 11 | 21 | 0% | 47.74%
2024-01-11 22:00 | 1 | 11 | 22 | 0% | 46.94%
2024-01-11 23:00 | 1 | 11 | 23 | 0% | 46.36%
2024-01-12 | 1 | 12 | 0 | 0% | 37.26%
2024-01-12 01:00 | 1 | 12 | 1 | 0% | 45.62%
2024-01-12 02:00 | 1 | 12 | 2 | 0% | 45.3%
2024-01-12 03:00 | 1 | 12 | 3 | 0% | 45.49%
2024-01-12 04:00 | 1 | 12 | 4 | 0% | 45.29%
2024-01-12 05:00 | 1 | 12 | 5 | 0% | 44.47%
2024-01-12 06:00 | 1 | 12 | 6 | 0% | 43.76%
2024-01-12 07:00 | 1 | 12 | 7 | 0% | 43.51%
2024-01-12 08:00 | 1 | 12 | 8 | 0% | 43.06%
2024-01-12 09:00 | 1 | 12 | 9 | 0% | 42.75%
2024-01-12 10:00 | 1 | 12 | 10 | 1.288% | 42.03%
2024-01-12 11:00 | 1 | 12 | 11 | 0.4755% | 40.97%
2024-01-12 12:00 | 1 | 12 | 12 | 0.6253% | 40.08%
2024-01-12 13:00 | 1 | 12 | 13 | 0.6206% | 38.81%
2024-01-12 14:00 | 1 | 12 | 14 | 0.3855% | 37.41%
2024-01-12 15:00 | 1 | 12 | 15 | 0% | 36.46%
2024-01-12 16:00 | 1 | 12 | 16 | 0% | 36.04%
2024-01-12 17:00 | 1 | 12 | 17 | 0% | 38.15%
2024-01-12 18:00 | 1 | 12 | 18 | 0% | 34.71%
2024-01-12 19:00 | 1 | 12 | 19 | 0% | 34.08%
2024-01-12 20:00 | 1 | 12 | 20 | 0% | 33.53%
2024-01-12 21:00 | 1 | 12 | 21 | 0% | 33.44%
2024-01-12 22:00 | 1 | 12 | 22 | 0% | 33.78%
2024-01-12 23:00 | 1 | 12 | 23 | 0% | 35.08%
2024-01-13 | 1 | 13 | 0 | 0% | 51.14%
2024-01-13 01:00 | 1 | 13 | 1 | 0% | 39.33%
2024-01-13 02:00 | 1 | 13 | 2 | 0% | 41.7%
2024-01-13 03:00 | 1 | 13 | 3 | 0% | 43.35%
2024-01-13 04:00 | 1 | 13 | 4 | 0% | 44.89%
2024-01-13 05:00 | 1 | 13 | 5 | 0% | 45.37%
2024-01-13 06:00 | 1 | 13 | 6 | 0% | 45.9%
2024-01-13 07:00 | 1 | 13 | 7 | 0% | 45.6%
2024-01-13 08:00 | 1 | 13 | 8 | 0% | 45.56%
2024-01-13 09:00 | 1 | 13 | 9 | 0% | 45.19%
2024-01-13 10:00 | 1 | 13 | 10 | 0% | 44.64%
2024-01-13 11:00 | 1 | 13 | 11 | 0% | 43.86%
2024-01-13 12:00 | 1 | 13 | 12 | 0% | 43.6%
2024-01-13 13:00 | 1 | 13 | 13 | 0% | 43.48%
2024-01-13 14:00 | 1 | 13 | 14 | 0% | 43.35%
2024-01-13 15:00 | 1 | 13 | 15 | 0% | 44.38%
2024-01-13 16:00 | 1 | 13 | 16 | 0% | 50.04%
2024-01-13 17:00 | 1 | 13 | 17 | 0% | 47.73%
2024-01-13 18:00 | 1 | 13 | 18 | 0% | 49.3%
2024-01-13 19:00 | 1 | 13 | 19 | 0% | 50.31%
2024-01-13 20:00 | 1 | 13 | 20 | 0% | 50.44%
2024-01-13 21:00 | 1 | 13 | 21 | 0% | 50.64%
2024-01-13 22:00 | 1 | 13 | 22 | 0% | 55.21%
2024-01-13 23:00 | 1 | 13 | 23 | 0% | 51.75%
2024-01-14 | 1 | 14 | 0 | 0% | 49.16%
2024-01-14 01:00 | 1 | 14 | 1 | 0% | 51.49%
2024-01-14 02:00 | 1 | 14 | 2 | 0% | 51.55%
2024-01-14 03:00 | 1 | 14 | 3 | 0% | 51.28%
2024-01-14 04:00 | 1 | 14 | 4 | 0% | 51.91%
2024-01-14 05:00 | 1 | 14 | 5 | 0% | 51.28%
2024-01-14 06:00 | 1 | 14 | 6 | 0% | 50.27%
2024-01-14 07:00 | 1 | 14 | 7 | 0% | 48.74%
2024-01-14 08:00 | 1 | 14 | 8 | 0% | 47.21%
2024-01-14 09:00 | 1 | 14 | 9 | 1.63% | 46.28%
2024-01-14 10:00 | 1 | 14 | 10 | 1.75% | 45.08%
2024-01-14 11:00 | 1 | 14 | 11 | 3.087% | 43.68%
2024-01-14 12:00 | 1 | 14 | 12 | 5.133% | 42.52%
2024-01-14 13:00 | 1 | 14 | 13 | 1.964% | 41.31%
2024-01-14 14:00 | 1 | 14 | 14 | 4.771% | 40.89%
2024-01-14 15:00 | 1 | 14 | 15 | 0.8066% | 40.96%
2024-01-14 16:00 | 1 | 14 | 16 | 0% | 41.25%
2024-01-14 17:00 | 1 | 14 | 17 | 0% | 42.45%
2024-01-14 18:00 | 1 | 14 | 18 | 0% | 42.95%
2024-01-14 19:00 | 1 | 14 | 19 | 0% | 44.17%
2024-01-14 20:00 | 1 | 14 | 20 | 0% | 45.31%
2024-01-14 21:00 | 1 | 14 | 21 | 0% | 45.99%
2024-01-14 22:00 | 1 | 14 | 22 | 0% | 46.85%
2024-01-14 23:00 | 1 | 14 | 23 | 0% | 47.83%
2024-01-15 | 1 | 15 | 0 | 0% | 48.38%
2024-01-15 01:00 | 1 | 15 | 1 | 0% | 49.03%
2024-01-15 02:00 | 1 | 15 | 2 | 0% | 48.48%
2024-01-15 03:00 | 1 | 15 | 3 | 0% | 48.07%
2024-01-15 04:00 | 1 | 15 | 4 | 0% | 47.06%
2024-01-15 05:00 | 1 | 15 | 5 | 0% | 46.19%
2024-01-15 06:00 | 1 | 15 | 6 | 0% | 45.26%
2024-01-15 07:00 | 1 | 15 | 7 | 0% | 44.26%
2024-01-15 08:00 | 1 | 15 | 8 | 0% | 43.79%
2024-01-15 09:00 | 1 | 15 | 9 | 4.981% | 44.5%
2024-01-15 10:00 | 1 | 15 | 10 | 14.39% | 44.08%
2024-01-15 11:00 | 1 | 15 | 11 | 21.83% | 43.26%
2024-01-15 12:00 | 1 | 15 | 12 | 23.77% | 43.44%
2024-01-15 13:00 | 1 | 15 | 13 | 20.27% | 43.87%
2024-01-15 14:00 | 1 | 15 | 14 | 12.01% | 44.72%
2024-01-15 15:00 | 1 | 15 | 15 | 1.824% | 46.34%
2024-01-15 16:00 | 1 | 15 | 16 | 0% | 47.95%
2024-01-15 17:00 | 1 | 15 | 17 | 0% | 48.5%
2024-01-15 18:00 | 1 | 15 | 18 | 0% | 49.5%
2024-01-15 19:00 | 1 | 15 | 19 | 0% | 49.79%
2024-01-15 20:00 | 1 | 15 | 20 | 0% | 49.67%
2024-01-15 21:00 | 1 | 15 | 21 | 0% | 49.96%
2024-01-15 22:00 | 1 | 15 | 22 | 0% | 49.61%
2024-01-15 23:00 | 1 | 15 | 23 | 0% | 49.05%
2024-01-16 | 1 | 16 | 0 | 0% | 52.53%
2024-01-16 01:00 | 1 | 16 | 1 | 0% | 48.34%
2024-01-16 02:00 | 1 | 16 | 2 | 0% | 48.79%
2024-01-16 03:00 | 1 | 16 | 3 | 0% | 49.57%
2024-01-16 04:00 | 1 | 16 | 4 | 0% | 49.84%
2024-01-16 05:00 | 1 | 16 | 5 | 0% | 50.3%
2024-01-16 06:00 | 1 | 16 | 6 | 0% | 50.5%
2024-01-16 07:00 | 1 | 16 | 7 | 0% | 50.31%
2024-01-16 08:00 | 1 | 16 | 8 | 0% | 49.76%
2024-01-16 09:00 | 1 | 16 | 9 | 2.172% | 49.49%
2024-01-16 10:00 | 1 | 16 | 10 | 11.34% | 49.52%
2024-01-16 11:00 | 1 | 16 | 11 | 8.086% | 49.08%
2024-01-16 12:00 | 1 | 16 | 12 | 5.342% | 48.33%
2024-01-16 13:00 | 1 | 16 | 13 | 2.971% | 47.89%
2024-01-16 14:00 | 1 | 16 | 14 | 2.063% | 47.27%
2024-01-16 15:00 | 1 | 16 | 15 | 0% | 47.05%
2024-01-16 16:00 | 1 | 16 | 16 | 0% | 47.51%
2024-01-16 17:00 | 1 | 16 | 17 | 0% | 47.71%
2024-01-16 18:00 | 1 | 16 | 18 | 0% | 48.08%
2024-01-16 19:00 | 1 | 16 | 19 | 0% | 48.53%
2024-01-16 20:00 | 1 | 16 | 20 | 0% | 48.83%
2024-01-16 21:00 | 1 | 16 | 21 | 0% | 48.66%
2024-01-16 22:00 | 1 | 16 | 22 | 0% | 48.02%
2024-01-16 23:00 | 1 | 16 | 23 | 0% | 47.76%
2024-01-17 | 1 | 17 | 0 | 0% | 39.92%
2024-01-17 01:00 | 1 | 17 | 1 | 0% | 48.41%
2024-01-17 02:00 | 1 | 17 | 2 | 0% | 49.27%
2024-01-17 03:00 | 1 | 17 | 3 | 0% | 50.02%
2024-01-17 04:00 | 1 | 17 | 4 | 0% | 50.68%
2024-01-17 05:00 | 1 | 17 | 5 | 0% | 51.08%
2024-01-17 06:00 | 1 | 17 | 6 | 0% | 52.05%
2024-01-17 07:00 | 1 | 17 | 7 | 0% | 52.28%
2024-01-17 08:00 | 1 | 17 | 8 | 0% | 51.83%
2024-01-17 09:00 | 1 | 17 | 9 | 4.854% | 52.09%
2024-01-17 10:00 | 1 | 17 | 10 | 14.43% | 51.54%
2024-01-17 11:00 | 1 | 17 | 11 | 7.799% | 50.86%
2024-01-17 12:00 | 1 | 17 | 12 | 4.147% | 49.84%
2024-01-17 13:00 | 1 | 17 | 13 | 3.543% | 49.42%
2024-01-17 14:00 | 1 | 17 | 14 | 3.662% | 49.16%
2024-01-17 15:00 | 1 | 17 | 15 | 0.9297% | 49.63%
2024-01-17 16:00 | 1 | 17 | 16 | 0% | 49.62%
2024-01-17 17:00 | 1 | 17 | 17 | 0% | 49.14%
2024-01-17 18:00 | 1 | 17 | 18 | 0% | 48.58%
2024-01-17 19:00 | 1 | 17 | 19 | 0% | 47.76%
2024-01-17 20:00 | 1 | 17 | 20 | 0% | 46.42%
2024-01-17 21:00 | 1 | 17 | 21 | 0% | 44.99%
2024-01-17 22:00 | 1 | 17 | 22 | 0% | 43.73%
2024-01-17 23:00 | 1 | 17 | 23 | 0% | 41.4%
2024-01-18 | 1 | 18 | 0 | 0% | 36.12%
2024-01-18 01:00 | 1 | 18 | 1 | 0% | 38.2%
2024-01-18 02:00 | 1 | 18 | 2 | 0% | 36.24%
2024-01-18 03:00 | 1 | 18 | 3 | 0% | 35.17%
2024-01-18 04:00 | 1 | 18 | 4 | 0% | 34.72%
2024-01-18 05:00 | 1 | 18 | 5 | 0% | 34.26%
2024-01-18 06:00 | 1 | 18 | 6 | 0% | 34.43%
2024-01-18 07:00 | 1 | 18 | 7 | 0% | 35.06%
2024-01-18 08:00 | 1 | 18 | 8 | 0% | 36.09%
2024-01-18 09:00 | 1 | 18 | 9 | 0.4414% | 36.55%
2024-01-18 10:00 | 1 | 18 | 10 | 0.956% | 37.03%
2024-01-18 11:00 | 1 | 18 | 11 | 1.191% | 36.76%
2024-01-18 12:00 | 1 | 18 | 12 | 1.598% | 36.76%
2024-01-18 13:00 | 1 | 18 | 13 | 1.435% | 35.99%
2024-01-18 14:00 | 1 | 18 | 14 | 1.5% | 36.26%
2024-01-18 15:00 | 1 | 18 | 15 | 0% | 37.62%
2024-01-18 16:00 | 1 | 18 | 16 | 0% | 38.55%
2024-01-18 17:00 | 1 | 18 | 17 | 0% | 38.91%
2024-01-18 18:00 | 1 | 18 | 18 | 0% | 38.94%
2024-01-18 19:00 | 1 | 18 | 19 | 0% | 39.94%
2024-01-18 20:00 | 1 | 18 | 20 | 0% | 37.49%
2024-01-18 21:00 | 1 | 18 | 21 | 0% | 36.69%
2024-01-18 22:00 | 1 | 18 | 22 | 0% | 36.37%
2024-01-18 23:00 | 1 | 18 | 23 | 0% | 35.88%
2024-01-19 | 1 | 19 | 0 | 0% | 24.37%
2024-01-19 01:00 | 1 | 19 | 1 | 0% | 35.92%
2024-01-19 02:00 | 1 | 19 | 2 | 0% | 35.44%
2024-01-19 03:00 | 1 | 19 | 3 | 0% | 35.13%
2024-01-19 04:00 | 1 | 19 | 4 | 0% | 35.71%
2024-01-19 05:00 | 1 | 19 | 5 | 0% | 36.09%
2024-01-19 06:00 | 1 | 19 | 6 | 0% | 36.36%
2024-01-19 07:00 | 1 | 19 | 7 | 0% | 36.42%
2024-01-19 08:00 | 1 | 19 | 8 | 0% | 36.46%
2024-01-19 09:00 | 1 | 19 | 9 | 1.427% | 36.18%
2024-01-19 10:00 | 1 | 19 | 10 | 2.915% | 35.24%
2024-01-19 11:00 | 1 | 19 | 11 | 4.032% | 34.29%
2024-01-19 12:00 | 1 | 19 | 12 | 3.796% | 33.16%
2024-01-19 13:00 | 1 | 19 | 13 | 3.177% | 32.4%
2024-01-19 14:00 | 1 | 19 | 14 | 1.874% | 32.67%
2024-01-19 15:00 | 1 | 19 | 15 | 0.7229% | 33.42%
2024-01-19 16:00 | 1 | 19 | 16 | 0% | 33.45%
2024-01-19 17:00 | 1 | 19 | 17 | 0% | 32.33%
2024-01-19 18:00 | 1 | 19 | 18 | 0% | 31.21%
2024-01-19 19:00 | 1 | 19 | 19 | 0% | 29.93%
2024-01-19 20:00 | 1 | 19 | 20 | 0% | 31.22%
2024-01-19 21:00 | 1 | 19 | 21 | 0% | 27.86%
2024-01-19 22:00 | 1 | 19 | 22 | 0% | 26.79%
2024-01-19 23:00 | 1 | 19 | 23 | 0% | 25.89%
2024-01-20 | 1 | 20 | 0 | 0% | 36.65%
2024-01-20 01:00 | 1 | 20 | 1 | 0% | 24.45%
2024-01-20 02:00 | 1 | 20 | 2 | 0% | 24.92%
2024-01-20 03:00 | 1 | 20 | 3 | 0% | 26.1%
2024-01-20 04:00 | 1 | 20 | 4 | 0% | 27.11%
2024-01-20 05:00 | 1 | 20 | 5 | 0% | 28.19%
2024-01-20 06:00 | 1 | 20 | 6 | 0% | 29.17%
2024-01-20 07:00 | 1 | 20 | 7 | 0% | 29.74%
2024-01-20 08:00 | 1 | 20 | 8 | 0% | 30.05%
2024-01-20 09:00 | 1 | 20 | 9 | 1.178% | 30.18%
2024-01-20 10:00 | 1 | 20 | 10 | 3.866% | 30.35%
2024-01-20 11:00 | 1 | 20 | 11 | 5.951% | 29.86%
2024-01-20 12:00 | 1 | 20 | 12 | 6.596% | 29.53%
2024-01-20 13:00 | 1 | 20 | 13 | 8.94% | 29.11%
2024-01-20 14:00 | 1 | 20 | 14 | 5.577% | 29.12%
2024-01-20 15:00 | 1 | 20 | 15 | 1.003% | 30.66%
2024-01-20 16:00 | 1 | 20 | 16 | 0% | 32.29%
2024-01-20 17:00 | 1 | 20 | 17 | 0% | 36.25%
2024-01-20 18:00 | 1 | 20 | 18 | 0% | 34.89%
2024-01-20 19:00 | 1 | 20 | 19 | 0% | 35.69%
2024-01-20 20:00 | 1 | 20 | 20 | 0% | 36.3%
2024-01-20 21:00 | 1 | 20 | 21 | 0% | 36.39%
2024-01-20 22:00 | 1 | 20 | 22 | 0% | 36.4%
2024-01-20 23:00 | 1 | 20 | 23 | 0% | 36.28%
2024-01-21 | 1 | 21 | 0 | 0% | 32.49%
2024-01-21 01:00 | 1 | 21 | 1 | 0% | 37.18%
2024-01-21 02:00 | 1 | 21 | 2 | 0% | 36.86%
2024-01-21 03:00 | 1 | 21 | 3 | 0% | 36.42%
2024-01-21 04:00 | 1 | 21 | 4 | 0% | 35.76%
2024-01-21 05:00 | 1 | 21 | 5 | 0% | 35.07%
2024-01-21 06:00 | 1 | 21 | 6 | 0% | 34.41%
2024-01-21 07:00 | 1 | 21 | 7 | 0% | 33.94%
2024-01-21 08:00 | 1 | 21 | 8 | 0% | 32.75%
2024-01-21 09:00 | 1 | 21 | 9 | 3.517% | 32.08%
2024-01-21 10:00 | 1 | 21 | 10 | 4.216% | 30.72%
2024-01-21 11:00 | 1 | 21 | 11 | 12.46% | 29.51%
2024-01-21 12:00 | 1 | 21 | 12 | 21.87% | 28.33%
2024-01-21 13:00 | 1 | 21 | 13 | 14.53% | 27.87%
2024-01-21 14:00 | 1 | 21 | 14 | 12.45% | 28.24%
2024-01-21 15:00 | 1 | 21 | 15 | 2.785% | 29.13%
2024-01-21 16:00 | 1 | 21 | 16 | 0% | 29.87%
2024-01-21 17:00 | 1 | 21 | 17 | 0% | 30.17%
2024-01-21 18:00 | 1 | 21 | 18 | 0% | 32.35%
2024-01-21 19:00 | 1 | 21 | 19 | 0% | 30.66%
2024-01-21 20:00 | 1 | 21 | 20 | 0% | 33.25%
2024-01-21 21:00 | 1 | 21 | 21 | 0% | 30.68%
2024-01-21 22:00 | 1 | 21 | 22 | 0% | 31%
2024-01-21 23:00 | 1 | 21 | 23 | 0% | 31.74%
2024-01-22 | 1 | 22 | 0 | 0% | 34.82%
2024-01-22 01:00 | 1 | 22 | 1 | 0% | 32.58%
2024-01-22 02:00 | 1 | 22 | 2 | 0% | 32.84%
2024-01-22 03:00 | 1 | 22 | 3 | 0% | 33.14%
2024-01-22 04:00 | 1 | 22 | 4 | 0% | 33.1%
2024-01-22 05:00 | 1 | 22 | 5 | 0% | 32.86%
2024-01-22 06:00 | 1 | 22 | 6 | 0% | 32.43%
2024-01-22 07:00 | 1 | 22 | 7 | 0% | 32.14%
2024-01-22 08:00 | 1 | 22 | 8 | 0% | 32.11%
2024-01-22 09:00 | 1 | 22 | 9 | 1.267% | 32.06%
2024-01-22 10:00 | 1 | 22 | 10 | 1.823% | 31.83%
2024-01-22 11:00 | 1 | 22 | 11 | 2.575% | 32.48%
2024-01-22 12:00 | 1 | 22 | 12 | 3.204% | 31.01%
2024-01-22 13:00 | 1 | 22 | 13 | 1.867% | 31.51%
2024-01-22 14:00 | 1 | 22 | 14 | 4.013% | 31.68%
2024-01-22 15:00 | 1 | 22 | 15 | 1.146% | 31.84%
2024-01-22 16:00 | 1 | 22 | 16 | 0% | 32.24%
2024-01-22 17:00 | 1 | 22 | 17 | 0% | 33.17%
2024-01-22 18:00 | 1 | 22 | 18 | 0% | 33.86%
2024-01-22 19:00 | 1 | 22 | 19 | 0% | 33.84%
2024-01-22 20:00 | 1 | 22 | 20 | 0% | 33.73%
2024-01-22 21:00 | 1 | 22 | 21 | 0% | 29.51%
2024-01-22 22:00 | 1 | 22 | 22 | 0% | 33.51%
2024-01-22 23:00 | 1 | 22 | 23 | 0% | 33.98%
2024-01-23 | 1 | 23 | 0 | 0% | 47.04%
2024-01-23 01:00 | 1 | 23 | 1 | 0% | 35.23%
2024-01-23 02:00 | 1 | 23 | 2 | 0% | 36.15%
2024-01-23 03:00 | 1 | 23 | 3 | 0% | 36.9%
2024-01-23 04:00 | 1 | 23 | 4 | 0% | 39.72%
2024-01-23 05:00 | 1 | 23 | 5 | 0% | 43.19%
2024-01-23 06:00 | 1 | 23 | 6 | 0% | 40.46%
2024-01-23 07:00 | 1 | 23 | 7 | 0% | 41%
2024-01-23 08:00 | 1 | 23 | 8 | 0% | 41.15%
2024-01-23 09:00 | 1 | 23 | 9 | 1.461% | 41.54%
2024-01-23 10:00 | 1 | 23 | 10 | 2.667% | 41.21%
2024-01-23 11:00 | 1 | 23 | 11 | 2.201% | 44.44%
2024-01-23 12:00 | 1 | 23 | 12 | 5.185% | 40.67%
2024-01-23 13:00 | 1 | 23 | 13 | 4.704% | 40.49%
2024-01-23 14:00 | 1 | 23 | 14 | 3.936% | 40.18%
2024-01-23 15:00 | 1 | 23 | 15 | 0.4881% | 40.66%
2024-01-23 16:00 | 1 | 23 | 16 | 0% | 41.2%
2024-01-23 17:00 | 1 | 23 | 17 | 0% | 41.67%
2024-01-23 18:00 | 1 | 23 | 18 | 0% | 41.72%
2024-01-23 19:00 | 1 | 23 | 19 | 0% | 38.63%
2024-01-23 20:00 | 1 | 23 | 20 | 0% | 42.17%
2024-01-23 21:00 | 1 | 23 | 21 | 0% | 43.01%
2024-01-23 22:00 | 1 | 23 | 22 | 0% | 43.93%
2024-01-23 23:00 | 1 | 23 | 23 | 0% | 45.01%
2024-01-24 | 1 | 24 | 0 | 0% | 42.72%
2024-01-24 01:00 | 1 | 24 | 1 | 0% | 47.72%
2024-01-24 02:00 | 1 | 24 | 2 | 0% | 48.72%
2024-01-24 03:00 | 1 | 24 | 3 | 0% | 48.95%
2024-01-24 04:00 | 1 | 24 | 4 | 0% | 48.9%
2024-01-24 05:00 | 1 | 24 | 5 | 0% | 48.67%
2024-01-24 06:00 | 1 | 24 | 6 | 0% | 47.84%
2024-01-24 07:00 | 1 | 24 | 7 | 0% | 46.53%
2024-01-24 08:00 | 1 | 24 | 8 | 0% | 47.01%
2024-01-24 09:00 | 1 | 24 | 9 | 1.119% | 43.99%
2024-01-24 10:00 | 1 | 24 | 10 | 2.437% | 42.88%
2024-01-24 11:00 | 1 | 24 | 11 | 2.538% | 41.72%
2024-01-24 12:00 | 1 | 24 | 12 | 1.265% | 40.75%
2024-01-24 13:00 | 1 | 24 | 13 | 3.207% | 40.22%
2024-01-24 14:00 | 1 | 24 | 14 | 1.462% | 40.33%
2024-01-24 15:00 | 1 | 24 | 15 | 0.4703% | 41.06%
2024-01-24 16:00 | 1 | 24 | 16 | 0% | 42.23%
2024-01-24 17:00 | 1 | 24 | 17 | 0% | 43.26%
2024-01-24 18:00 | 1 | 24 | 18 | 0% | 42.16%
2024-01-24 19:00 | 1 | 24 | 19 | 0% | 44.69%
2024-01-24 20:00 | 1 | 24 | 20 | 0% | 44.75%
2024-01-24 21:00 | 1 | 24 | 21 | 0% | 44.23%
2024-01-24 22:00 | 1 | 24 | 22 | 0% | 43.53%
2024-01-24 23:00 | 1 | 24 | 23 | 0% | 43.15%
2024-01-25 | 1 | 25 | 0 | 0% | 42.48%
2024-01-25 01:00 | 1 | 25 | 1 | 0% | 42.62%
2024-01-25 02:00 | 1 | 25 | 2 | 0% | 41.98%
2024-01-25 03:00 | 1 | 25 | 3 | 0% | 41.77%
2024-01-25 04:00 | 1 | 25 | 4 | 0% | 40.94%
2024-01-25 05:00 | 1 | 25 | 5 | 0% | 40.62%
2024-01-25 06:00 | 1 | 25 | 6 | 0% | 39.8%
2024-01-25 07:00 | 1 | 25 | 7 | 0% | 39.86%
2024-01-25 08:00 | 1 | 25 | 8 | 0% | 38.99%
2024-01-25 09:00 | 1 | 25 | 9 | 4.381% | 38.54%
2024-01-25 10:00 | 1 | 25 | 10 | 12.24% | 37.2%
2024-01-25 11:00 | 1 | 25 | 11 | 9.406% | 36.15%
2024-01-25 12:00 | 1 | 25 | 12 | 8.257% | 35.19%
2024-01-25 13:00 | 1 | 25 | 13 | 6.062% | 34.55%
2024-01-25 14:00 | 1 | 25 | 14 | 4.271% | 37.4%
2024-01-25 15:00 | 1 | 25 | 15 | 1.774% | 35.23%
2024-01-25 16:00 | 1 | 25 | 16 | 0% | 39.02%
2024-01-25 17:00 | 1 | 25 | 17 | 0% | 36.18%
2024-01-25 18:00 | 1 | 25 | 18 | 0% | 36.86%
2024-01-25 19:00 | 1 | 25 | 19 | 0% | 38.02%
2024-01-25 20:00 | 1 | 25 | 20 | 0% | 38.63%
2024-01-25 21:00 | 1 | 25 | 21 | 0% | 39.57%
2024-01-25 22:00 | 1 | 25 | 22 | 0% | 40.43%
2024-01-25 23:00 | 1 | 25 | 23 | 0% | 41.42%
2024-01-26 | 1 | 26 | 0 | 0% | 33.36%
2024-01-26 01:00 | 1 | 26 | 1 | 0% | 43.25%
2024-01-26 02:00 | 1 | 26 | 2 | 0% | 43.64%
2024-01-26 03:00 | 1 | 26 | 3 | 0% | 44.36%
2024-01-26 04:00 | 1 | 26 | 4 | 0% | 45.46%
2024-01-26 05:00 | 1 | 26 | 5 | 0% | 46.17%
2024-01-26 06:00 | 1 | 26 | 6 | 0% | 46.46%
2024-01-26 07:00 | 1 | 26 | 7 | 0% | 46.31%
2024-01-26 08:00 | 1 | 26 | 8 | 0% | 45.92%
2024-01-26 09:00 | 1 | 26 | 9 | 2.166% | 45.4%
2024-01-26 10:00 | 1 | 26 | 10 | 3.53% | 43.23%
2024-01-26 11:00 | 1 | 26 | 11 | 2.456% | 41.43%
2024-01-26 12:00 | 1 | 26 | 12 | 4.184% | 39.69%
2024-01-26 13:00 | 1 | 26 | 13 | 3.493% | 37.84%
2024-01-26 14:00 | 1 | 26 | 14 | 2.286% | 36.62%
2024-01-26 15:00 | 1 | 26 | 15 | 0.4458% | 35.64%
2024-01-26 16:00 | 1 | 26 | 16 | 0% | 34.95%
2024-01-26 17:00 | 1 | 26 | 17 | 0% | 34.17%
2024-01-26 18:00 | 1 | 26 | 18 | 0% | 34.07%
2024-01-26 19:00 | 1 | 26 | 19 | 0% | 33.8%
2024-01-26 20:00 | 1 | 26 | 20 | 0% | 33.48%
2024-01-26 21:00 | 1 | 26 | 21 | 0% | 33.39%
2024-01-26 22:00 | 1 | 26 | 22 | 0% | 33.42%
2024-01-26 23:00 | 1 | 26 | 23 | 0% | 33.52%
2024-01-27 | 1 | 27 | 0 | 0% | 48.38%
2024-01-27 01:00 | 1 | 27 | 1 | 0% | 33.19%
2024-01-27 02:00 | 1 | 27 | 2 | 0% | 32.73%
2024-01-27 03:00 | 1 | 27 | 3 | 0% | 32.66%
2024-01-27 04:00 | 1 | 27 | 4 | 0% | 32.59%
2024-01-27 05:00 | 1 | 27 | 5 | 0% | 32.32%
2024-01-27 06:00 | 1 | 27 | 6 | 0% | 31.32%
2024-01-27 07:00 | 1 | 27 | 7 | 0% | 30.93%
2024-01-27 08:00 | 1 | 27 | 8 | 0% | 30.64%
2024-01-27 09:00 | 1 | 27 | 9 | 1.496% | 31.12%
2024-01-27 10:00 | 1 | 27 | 10 | 1.452% | 31.22%
2024-01-27 11:00 | 1 | 27 | 11 | 1.852% | 31.53%
2024-01-27 12:00 | 1 | 27 | 12 | 1.52% | 32.35%
2024-01-27 13:00 | 1 | 27 | 13 | 1.12% | 33.69%
2024-01-27 14:00 | 1 | 27 | 14 | 1.125% | 35.55%
2024-01-27 15:00 | 1 | 27 | 15 | 1.556% | 37.02%
2024-01-27 16:00 | 1 | 27 | 16 | 0% | 38.76%
2024-01-27 17:00 | 1 | 27 | 17 | 0% | 40.45%
2024-01-27 18:00 | 1 | 27 | 18 | 0% | 41.74%
2024-01-27 19:00 | 1 | 27 | 19 | 0% | 43.11%
2024-01-27 20:00 | 1 | 27 | 20 | 0% | 44.42%
2024-01-27 21:00 | 1 | 27 | 21 | 0% | 46.01%
2024-01-27 22:00 | 1 | 27 | 22 | 0% | 47.08%
2024-01-27 23:00 | 1 | 27 | 23 | 0% | 47.81%
2024-01-28 | 1 | 28 | 0 | 0% | 39.89%
2024-01-28 01:00 | 1 | 28 | 1 | 0% | 47.8%
2024-01-28 02:00 | 1 | 28 | 2 | 0% | 48.23%
2024-01-28 03:00 | 1 | 28 | 3 | 0% | 48.23%
2024-01-28 04:00 | 1 | 28 | 4 | 0% | 47.94%
2024-01-28 05:00 | 1 | 28 | 5 | 0% | 47.47%
2024-01-28 06:00 | 1 | 28 | 6 | 0% | 47%
2024-01-28 07:00 | 1 | 28 | 7 | 0% | 46.06%
2024-01-28 08:00 | 1 | 28 | 8 | 0% | 45.18%
2024-01-28 09:00 | 1 | 28 | 9 | 0.5017% | 43.86%
2024-01-28 10:00 | 1 | 28 | 10 | 0.8902% | 42.23%
2024-01-28 11:00 | 1 | 28 | 11 | 2.639% | 40.18%
2024-01-28 12:00 | 1 | 28 | 12 | 2.804% | 38.57%
2024-01-28 13:00 | 1 | 28 | 13 | 4.418% | 37.45%
2024-01-28 14:00 | 1 | 28 | 14 | 1.297% | 37.36%
2024-01-28 15:00 | 1 | 28 | 15 | 0.3507% | 38.03%
2024-01-28 16:00 | 1 | 28 | 16 | 0% | 38.53%
2024-01-28 17:00 | 1 | 28 | 17 | 0% | 39.23%
2024-01-28 18:00 | 1 | 28 | 18 | 0% | 40.71%
2024-01-28 19:00 | 1 | 28 | 19 | 0% | 40.3%
2024-01-28 20:00 | 1 | 28 | 20 | 0% | 40.37%
2024-01-28 21:00 | 1 | 28 | 21 | 0% | 40.55%
2024-01-28 22:00 | 1 | 28 | 22 | 0% | 40.85%
2024-01-28 23:00 | 1 | 28 | 23 | 0% | 40.97%
2024-01-29 | 1 | 29 | 0 | 0% | 35.36%
2024-01-29 01:00 | 1 | 29 | 1 | 0% | 40.06%
2024-01-29 02:00 | 1 | 29 | 2 | 0% | 39.98%
2024-01-29 03:00 | 1 | 29 | 3 | 0% | 40.28%
2024-01-29 04:00 | 1 | 29 | 4 | 0% | 39.97%
2024-01-29 05:00 | 1 | 29 | 5 | 0% | 39.85%
2024-01-29 06:00 | 1 | 29 | 6 | 0% | 39.69%
2024-01-29 07:00 | 1 | 29 | 7 | 0% | 39.61%
2024-01-29 08:00 | 1 | 29 | 8 | 0% | 39.34%
2024-01-29 09:00 | 1 | 29 | 9 | 2.656% | 39.06%
2024-01-29 10:00 | 1 | 29 | 10 | 4.354% | 38.87%
2024-01-29 11:00 | 1 | 29 | 11 | 9.585% | 38.16%
2024-01-29 12:00 | 1 | 29 | 12 | 3.815% | 37.99%
2024-01-29 13:00 | 1 | 29 | 13 | 3.386% | 37.49%
2024-01-29 14:00 | 1 | 29 | 14 | 2.458% | 37.24%
2024-01-29 15:00 | 1 | 29 | 15 | 1.563% | 36.72%
2024-01-29 16:00 | 1 | 29 | 16 | 0% | 36.72%
2024-01-29 17:00 | 1 | 29 | 17 | 0% | 36.7%
2024-01-29 18:00 | 1 | 29 | 18 | 0% | 33.93%
2024-01-29 19:00 | 1 | 29 | 19 | 0% | 35.93%
2024-01-29 20:00 | 1 | 29 | 20 | 0% | 35.96%
2024-01-29 21:00 | 1 | 29 | 21 | 0% | 35.6%
2024-01-29 22:00 | 1 | 29 | 22 | 0% | 35.51%
2024-01-29 23:00 | 1 | 29 | 23 | 0% | 37.68%
2024-01-30 | 1 | 30 | 0 | 0% | 31.63%
2024-01-30 01:00 | 1 | 30 | 1 | 0% | 34.79%
2024-01-30 02:00 | 1 | 30 | 2 | 0% | 34.72%
2024-01-30 03:00 | 1 | 30 | 3 | 0% | 34.86%
2024-01-30 04:00 | 1 | 30 | 4 | 0% | 34.66%
2024-01-30 05:00 | 1 | 30 | 5 | 0% | 34.25%
2024-01-30 06:00 | 1 | 30 | 6 | 0% | 33.8%
2024-01-30 07:00 | 1 | 30 | 7 | 0% | 33.32%
2024-01-30 08:00 | 1 | 30 | 8 | 0% | 32.74%
2024-01-30 09:00 | 1 | 30 | 9 | 6.906% | 34.49%
2024-01-30 10:00 | 1 | 30 | 10 | 4.067% | 31.06%
2024-01-30 11:00 | 1 | 30 | 11 | 3.734% | 30.43%
2024-01-30 12:00 | 1 | 30 | 12 | 2.884% | 29.93%
2024-01-30 13:00 | 1 | 30 | 13 | 2.2% | 29.94%
2024-01-30 14:00 | 1 | 30 | 14 | 1.721% | 30.09%
2024-01-30 15:00 | 1 | 30 | 15 | 0.8563% | 30.8%
2024-01-30 16:00 | 1 | 30 | 16 | 0% | 31.87%
2024-01-30 17:00 | 1 | 30 | 17 | 0% | 32.35%
2024-01-30 18:00 | 1 | 30 | 18 | 0% | 32.49%
2024-01-30 19:00 | 1 | 30 | 19 | 0% | 32.12%
2024-01-30 20:00 | 1 | 30 | 20 | 0% | 31.68%
2024-01-30 21:00 | 1 | 30 | 21 | 0% | 34.18%
2024-01-30 22:00 | 1 | 30 | 22 | 0% | 31.46%
2024-01-30 23:00 | 1 | 30 | 23 | 0% | 31.27%
2024-01-31 | 1 | 31 | 0 | 0% | 34.92%
2024-01-31 01:00 | 1 | 31 | 1 | 0% | 31.19%
2024-01-31 02:00 | 1 | 31 | 2 | 0% | 31.16%
2024-01-31 03:00 | 1 | 31 | 3 | 0% | 30.8%
2024-01-31 04:00 | 1 | 31 | 4 | 0% | 30.13%
2024-01-31 05:00 | 1 | 31 | 5 | 0% | 29.54%
2024-01-31 06:00 | 1 | 31 | 6 | 0% | 29.25%
2024-01-31 07:00 | 1 | 31 | 7 | 0% | 29.49%
2024-01-31 08:00 | 1 | 31 | 8 | 0.868% | 29.14%
2024-01-31 09:00 | 1 | 31 | 9 | 6.05% | 30.15%
2024-01-31 10:00 | 1 | 31 | 10 | 5.566% | 30.18%
2024-01-31 11:00 | 1 | 31 | 11 | 7.513% | 30.02%
2024-01-31 12:00 | 1 | 31 | 12 | 5.815% | 29.75%
2024-01-31 13:00 | 1 | 31 | 13 | 6.007% | 29.94%
2024-01-31 14:00 | 1 | 31 | 14 | 4.406% | 30.55%
2024-01-31 15:00 | 1 | 31 | 15 | 2.967% | 32.21%
2024-01-31 16:00 | 1 | 31 | 16 | 0% | 33.85%
2024-01-31 17:00 | 1 | 31 | 17 | 0% | 35.15%
2024-01-31 18:00 | 1 | 31 | 18 | 0% | 36.32%
2024-01-31 19:00 | 1 | 31 | 19 | 0% | 36.11%
2024-01-31 20:00 | 1 | 31 | 20 | 0% | 36.08%
2024-01-31 21:00 | 1 | 31 | 21 | 0% | 35.75%
2024-01-31 22:00 | 1 | 31 | 22 | 0% | 34.61%
2024-01-31 23:00 | 1 | 31 | 23 | 0% | 34.42%
2024-02-01 | 2 | 1 | 0 | 0% | 32.8%
2024-02-01 01:00 | 2 | 1 | 1 | 0% | 34.49%
2024-02-01 02:00 | 2 | 1 | 2 | 0% | 34.2%
2024-02-01 03:00 | 2 | 1 | 3 | 0% | 34.49%
2024-02-01 04:00 | 2 | 1 | 4 | 0% | 34.78%
2024-02-01 05:00 | 2 | 1 | 5 | 0% | 35.03%
2024-02-01 06:00 | 2 | 1 | 6 | 0% | 35.15%
2024-02-01 07:00 | 2 | 1 | 7 | 0% | 34.69%
2024-02-01 08:00 | 2 | 1 | 8 | 0% | 34.06%
2024-02-01 09:00 | 2 | 1 | 9 | 0.3202% | 33.54%
2024-02-01 10:00 | 2 | 1 | 10 | 1.134% | 32.88%
2024-02-01 11:00 | 2 | 1 | 11 | 1.81% | 32.33%
2024-02-01 12:00 | 2 | 1 | 12 | 11.08% | 32.51%
2024-02-01 13:00 | 2 | 1 | 13 | 8.392% | 35.79%
2024-02-01 14:00 | 2 | 1 | 14 | 3.598% | 32.63%
2024-02-01 15:00 | 2 | 1 | 15 | 2.152% | 32.93%
2024-02-01 16:00 | 2 | 1 | 16 | 0% | 34.03%
2024-02-01 17:00 | 2 | 1 | 17 | 0% | 34.47%
2024-02-01 18:00 | 2 | 1 | 18 | 0% | 34.35%
2024-02-01 19:00 | 2 | 1 | 19 | 0% | 34.37%
2024-02-01 20:00 | 2 | 1 | 20 | 0% | 34.35%
2024-02-01 21:00 | 2 | 1 | 21 | 0% | 34.1%
2024-02-01 22:00 | 2 | 1 | 22 | 0% | 33.72%
2024-02-01 23:00 | 2 | 1 | 23 | 0% | 33.23%
2024-02-02 | 2 | 2 | 0 | 0% | 31.57%
2024-02-02 01:00 | 2 | 2 | 1 | 0% | 32.94%
2024-02-02 02:00 | 2 | 2 | 2 | 0% | 33.01%
2024-02-02 03:00 | 2 | 2 | 3 | 0% | 32.67%
2024-02-02 04:00 | 2 | 2 | 4 | 0% | 33.59%
2024-02-02 05:00 | 2 | 2 | 5 | 0% | 32.21%
2024-02-02 06:00 | 2 | 2 | 6 | 0% | 31.93%
2024-02-02 07:00 | 2 | 2 | 7 | 0% | 32%
2024-02-02 08:00 | 2 | 2 | 8 | 1.283% | 31.79%
2024-02-02 09:00 | 2 | 2 | 9 | 13.11% | 31.23%
2024-02-02 10:00 | 2 | 2 | 10 | 24.26% | 30.52%
2024-02-02 11:00 | 2 | 2 | 11 | 28.7% | 27.12%
2024-02-02 12:00 | 2 | 2 | 12 | 34.09% | 30.1%
2024-02-02 13:00 | 2 | 2 | 13 | 30.49% | 29.9%
2024-02-02 14:00 | 2 | 2 | 14 | 22.16% | 30.28%
2024-02-02 15:00 | 2 | 2 | 15 | 10.1% | 31.12%
2024-02-02 16:00 | 2 | 2 | 16 | 0% | 32%
2024-02-02 17:00 | 2 | 2 | 17 | 0% | 33.15%
2024-02-02 18:00 | 2 | 2 | 18 | 0% | 33.74%
2024-02-02 19:00 | 2 | 2 | 19 | 0% | 33.74%
2024-02-02 20:00 | 2 | 2 | 20 | 0% | 33.15%
2024-02-02 21:00 | 2 | 2 | 21 | 0% | 32.6%
2024-02-02 22:00 | 2 | 2 | 22 | 0% | 32.14%
2024-02-02 23:00 | 2 | 2 | 23 | 0% | 31.85%
2024-02-03 | 2 | 3 | 0 | 0% | 35.11%
2024-02-03 01:00 | 2 | 3 | 1 | 0% | 32.43%
2024-02-03 02:00 | 2 | 3 | 2 | 0% | 32.43%
2024-02-03 03:00 | 2 | 3 | 3 | 0% | 32.39%
2024-02-03 04:00 | 2 | 3 | 4 | 0% | 31.54%
2024-02-03 05:00 | 2 | 3 | 5 | 0% | 32.62%
2024-02-03 06:00 | 2 | 3 | 6 | 0% | 32.85%
2024-02-03 07:00 | 2 | 3 | 7 | 0% | 32.52%
2024-02-03 08:00 | 2 | 3 | 8 | 0.2755% | 32.42%
2024-02-03 09:00 | 2 | 3 | 9 | 11.27% | 31.61%
2024-02-03 10:00 | 2 | 3 | 10 | 21.81% | 30.31%
2024-02-03 11:00 | 2 | 3 | 11 | 27.71% | 28.68%
2024-02-03 12:00 | 2 | 3 | 12 | 28.3% | 27.52%
2024-02-03 13:00 | 2 | 3 | 13 | 23.45% | 27.48%
2024-02-03 14:00 | 2 | 3 | 14 | 19.24% | 28.09%
2024-02-03 15:00 | 2 | 3 | 15 | 5.435% | 29.65%
2024-02-03 16:00 | 2 | 3 | 16 | 0% | 31.22%
2024-02-03 17:00 | 2 | 3 | 17 | 0% | 32.98%
2024-02-03 18:00 | 2 | 3 | 18 | 0% | 34.3%
2024-02-03 19:00 | 2 | 3 | 19 | 0% | 34.84%
2024-02-03 20:00 | 2 | 3 | 20 | 0% | 35.35%
2024-02-03 21:00 | 2 | 3 | 21 | 0% | 35%
2024-02-03 22:00 | 2 | 3 | 22 | 0% | 35.23%
2024-02-03 23:00 | 2 | 3 | 23 | 0% | 35.91%
2024-02-04 | 2 | 4 | 0 | 0% | 42.77%
2024-02-04 01:00 | 2 | 4 | 1 | 0% | 35.41%
2024-02-04 02:00 | 2 | 4 | 2 | 0% | 35.74%
2024-02-04 03:00 | 2 | 4 | 3 | 0% | 35.77%
2024-02-04 04:00 | 2 | 4 | 4 | 0% | 36.16%
2024-02-04 05:00 | 2 | 4 | 5 | 0% | 37.38%
2024-02-04 06:00 | 2 | 4 | 6 | 0% | 35.83%
2024-02-04 07:00 | 2 | 4 | 7 | 0% | 35.3%
2024-02-04 08:00 | 2 | 4 | 8 | 0% | 34.82%
2024-02-04 09:00 | 2 | 4 | 9 | 4.2% | 34.09%
2024-02-04 10:00 | 2 | 4 | 10 | 8.441% | 33.16%
2024-02-04 11:00 | 2 | 4 | 11 | 8.214% | 31.96%
2024-02-04 12:00 | 2 | 4 | 12 | 6.967% | 31.4%
2024-02-04 13:00 | 2 | 4 | 13 | 7.28% | 30.91%
2024-02-04 14:00 | 2 | 4 | 14 | 3.512% | 32.92%
2024-02-04 15:00 | 2 | 4 | 15 | 2.562% | 31.57%
2024-02-04 16:00 | 2 | 4 | 16 | 0% | 33.08%
2024-02-04 17:00 | 2 | 4 | 17 | 0% | 34.63%
2024-02-04 18:00 | 2 | 4 | 18 | 0% | 36.66%
2024-02-04 19:00 | 2 | 4 | 19 | 0% | 38.18%
2024-02-04 20:00 | 2 | 4 | 20 | 0% | 38.85%
2024-02-04 21:00 | 2 | 4 | 21 | 0% | 39.81%
2024-02-04 22:00 | 2 | 4 | 22 | 0% | 40.6%
2024-02-04 23:00 | 2 | 4 | 23 | 0% | 42.01%
2024-02-05 | 2 | 5 | 0 | 0% | 33.6%
2024-02-05 01:00 | 2 | 5 | 1 | 0% | 43.69%
2024-02-05 02:00 | 2 | 5 | 2 | 0% | 44.49%
2024-02-05 03:00 | 2 | 5 | 3 | 0% | 46.66%
2024-02-05 04:00 | 2 | 5 | 4 | 0% | 45.81%
2024-02-05 05:00 | 2 | 5 | 5 | 0% | 46.2%
2024-02-05 06:00 | 2 | 5 | 6 | 0% | 46.21%
2024-02-05 07:00 | 2 | 5 | 7 | 0% | 45.04%
2024-02-05 08:00 | 2 | 5 | 8 | 2.274% | 43.21%
2024-02-05 09:00 | 2 | 5 | 9 | 15.21% | 40.5%
2024-02-05 10:00 | 2 | 5 | 10 | 26.12% | 37.63%
2024-02-05 11:00 | 2 | 5 | 11 | 34.13% | 35.19%
2024-02-05 12:00 | 2 | 5 | 12 | 36.3% | 32.63%
2024-02-05 13:00 | 2 | 5 | 13 | 26.71% | 32.68%
2024-02-05 14:00 | 2 | 5 | 14 | 7.275% | 31.1%
2024-02-05 15:00 | 2 | 5 | 15 | 2.965% | 31.84%
2024-02-05 16:00 | 2 | 5 | 16 | 0% | 33.4%
2024-02-05 17:00 | 2 | 5 | 17 | 0% | 34.44%
2024-02-05 18:00 | 2 | 5 | 18 | 0% | 35.55%
2024-02-05 19:00 | 2 | 5 | 19 | 0% | 36.35%
2024-02-05 20:00 | 2 | 5 | 20 | 0% | 36.19%
2024-02-05 21:00 | 2 | 5 | 21 | 0% | 35.4%
2024-02-05 22:00 | 2 | 5 | 22 | 0% | 34.88%
2024-02-05 23:00 | 2 | 5 | 23 | 0% | 34.33%
2024-02-06 | 2 | 6 | 0 | 0% | 30.2%
2024-02-06 01:00 | 2 | 6 | 1 | 0% | 32.74%
2024-02-06 02:00 | 2 | 6 | 2 | 0% | 32.06%
2024-02-06 03:00 | 2 | 6 | 3 | 0% | 31.44%
2024-02-06 04:00 | 2 | 6 | 4 | 0% | 30.67%
2024-02-06 05:00 | 2 | 6 | 5 | 0% | 30.2%
2024-02-06 06:00 | 2 | 6 | 6 | 0% | 29.45%
2024-02-06 07:00 | 2 | 6 | 7 | 0% | 28.61%
2024-02-06 08:00 | 2 | 6 | 8 | 2.099% | 27.97%
2024-02-06 09:00 | 2 | 6 | 9 | 14.38% | 27.16%
2024-02-06 10:00 | 2 | 6 | 10 | 25.45% | 25.89%
2024-02-06 11:00 | 2 | 6 | 11 | 33.5% | 24.69%
2024-02-06 12:00 | 2 | 6 | 12 | 35.98% | 24.37%
2024-02-06 13:00 | 2 | 6 | 13 | 29.2% | 24.38%
2024-02-06 14:00 | 2 | 6 | 14 | 18.35% | 24.78%
2024-02-06 15:00 | 2 | 6 | 15 | 10.02% | 26.13%
2024-02-06 16:00 | 2 | 6 | 16 | 0.7437% | 27.37%
2024-02-06 17:00 | 2 | 6 | 17 | 0% | 30.68%
2024-02-06 18:00 | 2 | 6 | 18 | 0% | 29.1%
2024-02-06 19:00 | 2 | 6 | 19 | 0% | 29.2%
2024-02-06 20:00 | 2 | 6 | 20 | 0% | 28.79%
2024-02-06 21:00 | 2 | 6 | 21 | 0% | 28.68%
2024-02-06 22:00 | 2 | 6 | 22 | 0% | 29.09%
2024-02-06 23:00 | 2 | 6 | 23 | 0% | 29.35%
2024-02-07 | 2 | 7 | 0 | 0% | 40.9%
2024-02-07 01:00 | 2 | 7 | 1 | 0% | 30.39%
2024-02-07 02:00 | 2 | 7 | 2 | 0% | 30.75%
2024-02-07 03:00 | 2 | 7 | 3 | 0% | 31.28%
2024-02-07 04:00 | 2 | 7 | 4 | 0% | 31.89%
2024-02-07 05:00 | 2 | 7 | 5 | 0% | 32.13%
2024-02-07 06:00 | 2 | 7 | 6 | 0% | 32.79%
2024-02-07 07:00 | 2 | 7 | 7 | 0% | 33.41%
2024-02-07 08:00 | 2 | 7 | 8 | 0.6261% | 33.37%
2024-02-07 09:00 | 2 | 7 | 9 | 2.137% | 32.63%
2024-02-07 10:00 | 2 | 7 | 10 | 3.769% | 32.12%
2024-02-07 11:00 | 2 | 7 | 11 | 4.519% | 31.7%
2024-02-07 12:00 | 2 | 7 | 12 | 4.677% | 31.62%
2024-02-07 13:00 | 2 | 7 | 13 | 4.243% | 31.84%
2024-02-07 14:00 | 2 | 7 | 14 | 3.476% | 33.05%
2024-02-07 15:00 | 2 | 7 | 15 | 1.761% | 35%
2024-02-07 16:00 | 2 | 7 | 16 | 0% | 36.8%
2024-02-07 17:00 | 2 | 7 | 17 | 0% | 37.83%
2024-02-07 18:00 | 2 | 7 | 18 | 0% | 38.51%
2024-02-07 19:00 | 2 | 7 | 19 | 0% | 38.36%
2024-02-07 20:00 | 2 | 7 | 20 | 0% | 37.62%
2024-02-07 21:00 | 2 | 7 | 21 | 0% | 37.5%
2024-02-07 22:00 | 2 | 7 | 22 | 0% | 37.97%
2024-02-07 23:00 | 2 | 7 | 23 | 0% | 38.98%
2024-02-08 | 2 | 8 | 0 | 0% | 43.88%
2024-02-08 01:00 | 2 | 8 | 1 | 0% | 41.66%
2024-02-08 02:00 | 2 | 8 | 2 | 0% | 42.32%
2024-02-08 03:00 | 2 | 8 | 3 | 0% | 43%
2024-02-08 04:00 | 2 | 8 | 4 | 0% | 43.55%
2024-02-08 05:00 | 2 | 8 | 5 | 0% | 43.84%
2024-02-08 06:00 | 2 | 8 | 6 | 0% | 43.79%
2024-02-08 07:00 | 2 | 8 | 7 | 0% | 43.99%
2024-02-08 08:00 | 2 | 8 | 8 | 1.174% | 43.74%
2024-02-08 09:00 | 2 | 8 | 9 | 1.36% | 42.71%
2024-02-08 10:00 | 2 | 8 | 10 | 2.124% | 42.37%
2024-02-08 11:00 | 2 | 8 | 11 | 4.124% | 41.95%
2024-02-08 12:00 | 2 | 8 | 12 | 5.39% | 41.59%
2024-02-08 13:00 | 2 | 8 | 13 | 7.956% | 41.4%
2024-02-08 14:00 | 2 | 8 | 14 | 11.37% | 41.81%
2024-02-08 15:00 | 2 | 8 | 15 | 3.708% | 41.72%
2024-02-08 16:00 | 2 | 8 | 16 | 0% | 42.25%
2024-02-08 17:00 | 2 | 8 | 17 | 0% | 44.55%
2024-02-08 18:00 | 2 | 8 | 18 | 0% | 44.02%
2024-02-08 19:00 | 2 | 8 | 19 | 0% | 44.66%
2024-02-08 20:00 | 2 | 8 | 20 | 0% | 44.49%
2024-02-08 21:00 | 2 | 8 | 21 | 0% | 43.99%
2024-02-08 22:00 | 2 | 8 | 22 | 0% | 43.65%
2024-02-08 23:00 | 2 | 8 | 23 | 0% | 43.46%
2024-02-09 | 2 | 9 | 0 | 0% | 49.5%
2024-02-09 01:00 | 2 | 9 | 1 | 0% | 46.8%
2024-02-09 02:00 | 2 | 9 | 2 | 0% | 44.72%
2024-02-09 03:00 | 2 | 9 | 3 | 0% | 45.07%
2024-02-09 04:00 | 2 | 9 | 4 | 0% | 46.51%
2024-02-09 05:00 | 2 | 9 | 5 | 0% | 46.16%
2024-02-09 06:00 | 2 | 9 | 6 | 0% | 46.64%
2024-02-09 07:00 | 2 | 9 | 7 | 0% | 48.76%
2024-02-09 08:00 | 2 | 9 | 8 | 0.2473% | 46.7%
2024-02-09 09:00 | 2 | 9 | 9 | 0.2002% | 45.93%
2024-02-09 10:00 | 2 | 9 | 10 | 1.843% | 47.5%
2024-02-09 11:00 | 2 | 9 | 11 | 2.989% | 44.96%
2024-02-09 12:00 | 2 | 9 | 12 | 2.447% | 44.71%
2024-02-09 13:00 | 2 | 9 | 13 | 2.629% | 45.2%
2024-02-09 14:00 | 2 | 9 | 14 | 1.846% | 45.75%
2024-02-09 15:00 | 2 | 9 | 15 | 1.087% | 48.64%
2024-02-09 16:00 | 2 | 9 | 16 | 0% | 43.8%
2024-02-09 17:00 | 2 | 9 | 17 | 0% | 48.98%
2024-02-09 18:00 | 2 | 9 | 18 | 0% | 50.27%
2024-02-09 19:00 | 2 | 9 | 19 | 0% | 50.89%
2024-02-09 20:00 | 2 | 9 | 20 | 0% | 51.28%
2024-02-09 21:00 | 2 | 9 | 21 | 0% | 51%
2024-02-09 22:00 | 2 | 9 | 22 | 0% | 50.16%
2024-02-09 23:00 | 2 | 9 | 23 | 0% | 49.45%
2024-02-10 | 2 | 10 | 0 | 0% | 39.57%
2024-02-10 01:00 | 2 | 10 | 1 | 0% | 48.75%
2024-02-10 02:00 | 2 | 10 | 2 | 0% | 48.76%
2024-02-10 03:00 | 2 | 10 | 3 | 0% | 48.88%
2024-02-10 04:00 | 2 | 10 | 4 | 0% | 48.82%
2024-02-10 05:00 | 2 | 10 | 5 | 0% | 49.01%
2024-02-10 06:00 | 2 | 10 | 6 | 0% | 49.17%
2024-02-10 07:00 | 2 | 10 | 7 | 0% | 52.11%
2024-02-10 08:00 | 2 | 10 | 8 | 0% | 50.45%
2024-02-10 09:00 | 2 | 10 | 9 | 1.435% | 45.7%
2024-02-10 10:00 | 2 | 10 | 10 | 4.631% | 43.92%
2024-02-10 11:00 | 2 | 10 | 11 | 6.824% | 41.97%
2024-02-10 12:00 | 2 | 10 | 12 | 7.874% | 40.85%
2024-02-10 13:00 | 2 | 10 | 13 | 7.252% | 39.82%
2024-02-10 14:00 | 2 | 10 | 14 | 7.557% | 39.89%
2024-02-10 15:00 | 2 | 10 | 15 | 4.237% | 40.6%
2024-02-10 16:00 | 2 | 10 | 16 | 0% | 42.26%
2024-02-10 17:00 | 2 | 10 | 17 | 0% | 43.48%
2024-02-10 18:00 | 2 | 10 | 18 | 0% | 45.04%
2024-02-10 19:00 | 2 | 10 | 19 | 0% | 45.16%
2024-02-10 20:00 | 2 | 10 | 20 | 0% | 44.62%
2024-02-10 21:00 | 2 | 10 | 21 | 0% | 43.18%
2024-02-10 22:00 | 2 | 10 | 22 | 0% | 41.63%
2024-02-10 23:00 | 2 | 10 | 23 | 0% | 40.35%
2024-02-11 | 2 | 11 | 0 | 0% | 46.43%
2024-02-11 01:00 | 2 | 11 | 1 | 0% | 39%
2024-02-11 02:00 | 2 | 11 | 2 | 0% | 38.85%
2024-02-11 03:00 | 2 | 11 | 3 | 0% | 38.71%
2024-02-11 04:00 | 2 | 11 | 4 | 0% | 38.99%
2024-02-11 05:00 | 2 | 11 | 5 | 0% | 39.38%
2024-02-11 06:00 | 2 | 11 | 6 | 0% | 39.6%
2024-02-11 07:00 | 2 | 11 | 7 | 0% | 39.4%
2024-02-11 08:00 | 2 | 11 | 8 | 1.916% | 38.03%
2024-02-11 09:00 | 2 | 11 | 9 | 2.388% | 35.74%
2024-02-11 10:00 | 2 | 11 | 10 | 2.492% | 33.41%
2024-02-11 11:00 | 2 | 11 | 11 | 8.793% | 30.94%
2024-02-11 12:00 | 2 | 11 | 12 | 9.229% | 29.15%
2024-02-11 13:00 | 2 | 11 | 13 | 8.49% | 28.79%
2024-02-11 14:00 | 2 | 11 | 14 | 4.959% | 29.51%
2024-02-11 15:00 | 2 | 11 | 15 | 4.109% | 30.74%
2024-02-11 16:00 | 2 | 11 | 16 | 0% | 32.7%
2024-02-11 17:00 | 2 | 11 | 17 | 0% | 35.26%
2024-02-11 18:00 | 2 | 11 | 18 | 0% | 40.45%
2024-02-11 19:00 | 2 | 11 | 19 | 0% | 40.14%
2024-02-11 20:00 | 2 | 11 | 20 | 0% | 41.85%
2024-02-11 21:00 | 2 | 11 | 21 | 0% | 43.4%
2024-02-11 22:00 | 2 | 11 | 22 | 0% | 44.95%
2024-02-11 23:00 | 2 | 11 | 23 | 0% | 45.05%
2024-02-12 | 2 | 12 | 0 | 0% | 40.41%
2024-02-12 01:00 | 2 | 12 | 1 | 0% | 49.3%
2024-02-12 02:00 | 2 | 12 | 2 | 0% | 47.25%
2024-02-12 03:00 | 2 | 12 | 3 | 0% | 47.42%
2024-02-12 04:00 | 2 | 12 | 4 | 0% | 47.66%
2024-02-12 05:00 | 2 | 12 | 5 | 0% | 47.69%
2024-02-12 06:00 | 2 | 12 | 6 | 0% | 46.84%
2024-02-12 07:00 | 2 | 12 | 7 | 0% | 46.26%
2024-02-12 08:00 | 2 | 12 | 8 | 0% | 44.79%
2024-02-12 09:00 | 2 | 12 | 9 | 2.179% | 43.36%
2024-02-12 10:00 | 2 | 12 | 10 | 14.74% | 41.58%
2024-02-12 11:00 | 2 | 12 | 11 | 23.76% | 39.83%
2024-02-12 12:00 | 2 | 12 | 12 | 39.26% | 38.44%
2024-02-12 13:00 | 2 | 12 | 13 | 37.07% | 37.2%
2024-02-12 14:00 | 2 | 12 | 14 | 28.07% | 36.83%
2024-02-12 15:00 | 2 | 12 | 15 | 14.7% | 37.11%
2024-02-12 16:00 | 2 | 12 | 16 | 1.317% | 38.4%
2024-02-12 17:00 | 2 | 12 | 17 | 0% | 39.2%
2024-02-12 18:00 | 2 | 12 | 18 | 0% | 40.35%
2024-02-12 19:00 | 2 | 12 | 19 | 0% | 43.63%
2024-02-12 20:00 | 2 | 12 | 20 | 0% | 43.31%
2024-02-12 21:00 | 2 | 12 | 21 | 0% | 40.55%
2024-02-12 22:00 | 2 | 12 | 22 | 0% | 40.37%
2024-02-12 23:00 | 2 | 12 | 23 | 0% | 40.51%
2024-02-13 | 2 | 13 | 0 | 0% | 25.62%
2024-02-13 01:00 | 2 | 13 | 1 | 0% | 40.28%
2024-02-13 02:00 | 2 | 13 | 2 | 0% | 40.17%
2024-02-13 03:00 | 2 | 13 | 3 | 0% | 40.32%
2024-02-13 04:00 | 2 | 13 | 4 | 0% | 40.06%
2024-02-13 05:00 | 2 | 13 | 5 | 0% | 40.13%
2024-02-13 06:00 | 2 | 13 | 6 | 0% | 40.13%
2024-02-13 07:00 | 2 | 13 | 7 | 0% | 39.89%
2024-02-13 08:00 | 2 | 13 | 8 | 4.016% | 38.97%
2024-02-13 09:00 | 2 | 13 | 9 | 15.93% | 37.25%
2024-02-13 10:00 | 2 | 13 | 10 | 31.98% | 35.59%
2024-02-13 11:00 | 2 | 13 | 11 | 40.56% | 33.92%
2024-02-13 12:00 | 2 | 13 | 12 | 37.78% | 32.38%
2024-02-13 13:00 | 2 | 13 | 13 | 31.18% | 30.92%
2024-02-13 14:00 | 2 | 13 | 14 | 20.31% | 30.24%
2024-02-13 15:00 | 2 | 13 | 15 | 11.52% | 30.12%
2024-02-13 16:00 | 2 | 13 | 16 | 0.8923% | 30.85%
2024-02-13 17:00 | 2 | 13 | 17 | 0% | 33.01%
2024-02-13 18:00 | 2 | 13 | 18 | 0% | 32.71%
2024-02-13 19:00 | 2 | 13 | 19 | 0% | 32.31%
2024-02-13 20:00 | 2 | 13 | 20 | 0% | 31.51%
2024-02-13 21:00 | 2 | 13 | 21 | 0% | 29.94%
2024-02-13 22:00 | 2 | 13 | 22 | 0% | 30.54%
2024-02-13 23:00 | 2 | 13 | 23 | 0% | 30.33%
2024-02-14 | 2 | 14 | 0 | 0% | 29.39%
2024-02-14 01:00 | 2 | 14 | 1 | 0% | 25.38%
2024-02-14 02:00 | 2 | 14 | 2 | 0% | 23.1%
2024-02-14 03:00 | 2 | 14 | 3 | 0% | 22.38%
2024-02-14 04:00 | 2 | 14 | 4 | 0% | 21.75%
2024-02-14 05:00 | 2 | 14 | 5 | 0% | 21.17%
2024-02-14 06:00 | 2 | 14 | 6 | 0% | 21.01%
2024-02-14 07:00 | 2 | 14 | 7 | 0% | 20.72%
2024-02-14 08:00 | 2 | 14 | 8 | 4.534% | 21.3%
2024-02-14 09:00 | 2 | 14 | 9 | 17.36% | 18.42%
2024-02-14 10:00 | 2 | 14 | 10 | 17.58% | 17.2%
2024-02-14 11:00 | 2 | 14 | 11 | 14.57% | 15.99%
2024-02-14 12:00 | 2 | 14 | 12 | 11.95% | 15.4%
2024-02-14 13:00 | 2 | 14 | 13 | 9.738% | 15.37%
2024-02-14 14:00 | 2 | 14 | 14 | 11.59% | 16.04%
2024-02-14 15:00 | 2 | 14 | 15 | 8.045% | 17.41%
2024-02-14 16:00 | 2 | 14 | 16 | 0.7898% | 19.34%
2024-02-14 17:00 | 2 | 14 | 17 | 0% | 21.87%
2024-02-14 18:00 | 2 | 14 | 18 | 0% | 24.23%
2024-02-14 19:00 | 2 | 14 | 19 | 0% | 25.99%
2024-02-14 20:00 | 2 | 14 | 20 | 0% | 28.41%
2024-02-14 21:00 | 2 | 14 | 21 | 0% | 27.1%
2024-02-14 22:00 | 2 | 14 | 22 | 0% | 27.44%
2024-02-14 23:00 | 2 | 14 | 23 | 0% | 28.06%
2024-02-15 | 2 | 15 | 0 | 0% | 43.75%
2024-02-15 01:00 | 2 | 15 | 1 | 0% | 29.81%
2024-02-15 02:00 | 2 | 15 | 2 | 0% | 30.52%
2024-02-15 03:00 | 2 | 15 | 3 | 0% | 31.15%
2024-02-15 04:00 | 2 | 15 | 4 | 0% | 31.89%
2024-02-15 05:00 | 2 | 15 | 5 | 0% | 32.73%
2024-02-15 06:00 | 2 | 15 | 6 | 0% | 33.7%
2024-02-15 07:00 | 2 | 15 | 7 | 0% | 34.14%
2024-02-15 08:00 | 2 | 15 | 8 | 0.2881% | 34.49%
2024-02-15 09:00 | 2 | 15 | 9 | 2.248% | 34.45%
2024-02-15 10:00 | 2 | 15 | 10 | 3.575% | 35.98%
2024-02-15 11:00 | 2 | 15 | 11 | 3.989% | 33.59%
2024-02-15 12:00 | 2 | 15 | 12 | 5.305% | 33.67%
2024-02-15 13:00 | 2 | 15 | 13 | 5.425% | 34.2%
2024-02-15 14:00 | 2 | 15 | 14 | 3.392% | 34.15%
2024-02-15 15:00 | 2 | 15 | 15 | 3.454% | 35.3%
2024-02-15 16:00 | 2 | 15 | 16 | 0.245% | 37.29%
2024-02-15 17:00 | 2 | 15 | 17 | 0% | 39.52%
2024-02-15 18:00 | 2 | 15 | 18 | 0% | 41.31%
2024-02-15 19:00 | 2 | 15 | 19 | 0% | 42.65%
2024-02-15 20:00 | 2 | 15 | 20 | 0% | 45.72%
2024-02-15 21:00 | 2 | 15 | 21 | 0% | 43.88%
2024-02-15 22:00 | 2 | 15 | 22 | 0% | 44.18%
2024-02-15 23:00 | 2 | 15 | 23 | 0% | 43.66%
2024-02-16 | 2 | 16 | 0 | 0% | 40.28%
2024-02-16 01:00 | 2 | 16 | 1 | 0% | 43.66%
2024-02-16 02:00 | 2 | 16 | 2 | 0% | 43.41%
2024-02-16 03:00 | 2 | 16 | 3 | 0% | 42.57%
2024-02-16 04:00 | 2 | 16 | 4 | 0% | 41.89%
2024-02-16 05:00 | 2 | 16 | 5 | 0% | 41.82%
2024-02-16 06:00 | 2 | 16 | 6 | 0% | 41.77%
2024-02-16 07:00 | 2 | 16 | 7 | 0% | 41.81%
2024-02-16 08:00 | 2 | 16 | 8 | 0% | 40.84%
2024-02-16 09:00 | 2 | 16 | 9 | 0.8357% | 40.11%
2024-02-16 10:00 | 2 | 16 | 10 | 2.617% | 39.07%
2024-02-16 11:00 | 2 | 16 | 11 | 3.314% | 37.73%
2024-02-16 12:00 | 2 | 16 | 12 | 2.689% | 36.22%
2024-02-16 13:00 | 2 | 16 | 13 | 2.865% | 35.27%
2024-02-16 14:00 | 2 | 16 | 14 | 4.262% | 34.75%
2024-02-16 15:00 | 2 | 16 | 15 | 2.995% | 35.11%
2024-02-16 16:00 | 2 | 16 | 16 | 0.229% | 36.1%
2024-02-16 17:00 | 2 | 16 | 17 | 0% | 37.79%
2024-02-16 18:00 | 2 | 16 | 18 | 0% | 38.95%
2024-02-16 19:00 | 2 | 16 | 19 | 0% | 39.86%
2024-02-16 20:00 | 2 | 16 | 20 | 0% | 40.19%
2024-02-16 21:00 | 2 | 16 | 21 | 0% | 40.11%
2024-02-16 22:00 | 2 | 16 | 22 | 0% | 40.26%
2024-02-16 23:00 | 2 | 16 | 23 | 0% | 40.29%
2024-02-17 | 2 | 17 | 0 | 0% | 42.12%
2024-02-17 01:00 | 2 | 17 | 1 | 0% | 40.31%
2024-02-17 02:00 | 2 | 17 | 2 | 0% | 40.29%
2024-02-17 03:00 | 2 | 17 | 3 | 0% | 40.5%
2024-02-17 04:00 | 2 | 17 | 4 | 0% | 40.3%
2024-02-17 05:00 | 2 | 17 | 5 | 0% | 40.51%
2024-02-17 06:00 | 2 | 17 | 6 | 0% | 40.56%
2024-02-17 07:00 | 2 | 17 | 7 | 0% | 40.2%
2024-02-17 08:00 | 2 | 17 | 8 | 1.762% | 39.64%
2024-02-17 09:00 | 2 | 17 | 9 | 5.657% | 38.19%
2024-02-17 10:00 | 2 | 17 | 10 | 3.468% | 36.92%
2024-02-17 11:00 | 2 | 17 | 11 | 3.352% | 35.9%
2024-02-17 12:00 | 2 | 17 | 12 | 4.148% | 35.83%
2024-02-17 13:00 | 2 | 17 | 13 | 4.335% | 36.08%
2024-02-17 14:00 | 2 | 17 | 14 | 4.028% | 35.74%
2024-02-17 15:00 | 2 | 17 | 15 | 2.722% | 35.23%
2024-02-17 16:00 | 2 | 17 | 16 | 0.5643% | 35.57%
2024-02-17 17:00 | 2 | 17 | 17 | 0% | 36.4%
2024-02-17 18:00 | 2 | 17 | 18 | 0% | 32.47%
2024-02-17 19:00 | 2 | 17 | 19 | 0% | 38.2%
2024-02-17 20:00 | 2 | 17 | 20 | 0% | 38.42%
2024-02-17 21:00 | 2 | 17 | 21 | 0% | 39.38%
2024-02-17 22:00 | 2 | 17 | 22 | 0% | 40.87%
2024-02-17 23:00 | 2 | 17 | 23 | 0% | 41.77%
2024-02-18 | 2 | 18 | 0 | 0% | 40.66%
2024-02-18 01:00 | 2 | 18 | 1 | 0% | 40.66%
2024-02-18 02:00 | 2 | 18 | 2 | 0% | 43.16%
2024-02-18 03:00 | 2 | 18 | 3 | 0% | 43.85%
2024-02-18 04:00 | 2 | 18 | 4 | 0% | 44.28%
2024-02-18 05:00 | 2 | 18 | 5 | 0% | 44.1%
2024-02-18 06:00 | 2 | 18 | 6 | 0% | 47.09%
2024-02-18 07:00 | 2 | 18 | 7 | 0% | 43.93%
2024-02-18 08:00 | 2 | 18 | 8 | 2.717% | 43.18%
2024-02-18 09:00 | 2 | 18 | 9 | 5.959% | 42.3%
2024-02-18 10:00 | 2 | 18 | 10 | 4.658% | 40.55%
2024-02-18 11:00 | 2 | 18 | 11 | 1.363% | 39.41%
2024-02-18 12:00 | 2 | 18 | 12 | 7.725% | 38.7%
2024-02-18 13:00 | 2 | 18 | 13 | 12.52% | 38.55%
2024-02-18 14:00 | 2 | 18 | 14 | 16.74% | 38.42%
2024-02-18 15:00 | 2 | 18 | 15 | 8.308% | 38.87%
2024-02-18 16:00 | 2 | 18 | 16 | 1.408% | 39.95%
2024-02-18 17:00 | 2 | 18 | 17 | 0% | 41.64%
2024-02-18 18:00 | 2 | 18 | 18 | 0% | 42.3%
2024-02-18 19:00 | 2 | 18 | 19 | 0% | 42.68%
2024-02-18 20:00 | 2 | 18 | 20 | 0% | 42.92%
2024-02-18 21:00 | 2 | 18 | 21 | 0% | 42.93%
2024-02-18 22:00 | 2 | 18 | 22 | 0% | 42.44%
2024-02-18 23:00 | 2 | 18 | 23 | 0% | 41.94%
2024-02-19 | 2 | 19 | 0 | 0% | 28.69%
2024-02-19 01:00 | 2 | 19 | 1 | 0% | 40.14%
2024-02-19 02:00 | 2 | 19 | 2 | 0% | 39.19%
2024-02-19 03:00 | 2 | 19 | 3 | 0% | 38.48%
2024-02-19 04:00 | 2 | 19 | 4 | 0% | 37.56%
2024-02-19 05:00 | 2 | 19 | 5 | 0% | 34.7%
2024-02-19 06:00 | 2 | 19 | 6 | 0% | 35.64%
2024-02-19 07:00 | 2 | 19 | 7 | 0% | 34.5%
2024-02-19 08:00 | 2 | 19 | 8 | 0.9811% | 32.87%
2024-02-19 09:00 | 2 | 19 | 9 | 6.446% | 31.47%
2024-02-19 10:00 | 2 | 19 | 10 | 13.13% | 29.62%
2024-02-19 11:00 | 2 | 19 | 11 | 28.45% | 28.26%
2024-02-19 12:00 | 2 | 19 | 12 | 30.56% | 27.81%
2024-02-19 13:00 | 2 | 19 | 13 | 23.03% | 27.83%
2024-02-19 14:00 | 2 | 19 | 14 | 28.77% | 27.77%
2024-02-19 15:00 | 2 | 19 | 15 | 21.07% | 28.28%
2024-02-19 16:00 | 2 | 19 | 16 | 5.713% | 29.45%
2024-02-19 17:00 | 2 | 19 | 17 | 0% | 31.3%
2024-02-19 18:00 | 2 | 19 | 18 | 0% | 32.31%
2024-02-19 19:00 | 2 | 19 | 19 | 0% | 32.78%
2024-02-19 20:00 | 2 | 19 | 20 | 0% | 32.41%
2024-02-19 21:00 | 2 | 19 | 21 | 0% | 31.66%
2024-02-19 22:00 | 2 | 19 | 22 | 0% | 30.82%
2024-02-19 23:00 | 2 | 19 | 23 | 0% | 28.43%
2024-02-20 | 2 | 20 | 0 | 0% | 45.75%
2024-02-20 01:00 | 2 | 20 | 1 | 0% | 32.32%
2024-02-20 02:00 | 2 | 20 | 2 | 0% | 33.59%
2024-02-20 03:00 | 2 | 20 | 3 | 0% | 35.23%
2024-02-20 04:00 | 2 | 20 | 4 | 0% | 37.24%
2024-02-20 05:00 | 2 | 20 | 5 | 0% | 39.11%
2024-02-20 06:00 | 2 | 20 | 6 | 0% | 40.45%
2024-02-20 07:00 | 2 | 20 | 7 | 0% | 41.43%
2024-02-20 08:00 | 2 | 20 | 8 | 2.893% | 41.43%
2024-02-20 09:00 | 2 | 20 | 9 | 4.72% | 40.83%
2024-02-20 10:00 | 2 | 20 | 10 | 4.12% | 39.34%
2024-02-20 11:00 | 2 | 20 | 11 | 4.614% | 37.93%
2024-02-20 12:00 | 2 | 20 | 12 | 3.375% | 37.64%
2024-02-20 13:00 | 2 | 20 | 13 | 3.922% | 38.06%
2024-02-20 14:00 | 2 | 20 | 14 | 3.587% | 38.81%
2024-02-20 15:00 | 2 | 20 | 15 | 3.203% | 39.7%
2024-02-20 16:00 | 2 | 20 | 16 | 0.7239% | 41.21%
2024-02-20 17:00 | 2 | 20 | 17 | 0% | 43.49%
2024-02-20 18:00 | 2 | 20 | 18 | 0% | 45.62%
2024-02-20 19:00 | 2 | 20 | 19 | 0% | 46.74%
2024-02-20 20:00 | 2 | 20 | 20 | 0% | 47.22%
2024-02-20 21:00 | 2 | 20 | 21 | 0% | 47.27%
2024-02-20 22:00 | 2 | 20 | 22 | 0% | 47.31%
2024-02-20 23:00 | 2 | 20 | 23 | 0% | 46.74%
2024-02-21 | 2 | 21 | 0 | 0% | 35.51%
2024-02-21 01:00 | 2 | 21 | 1 | 0% | 49.71%
2024-02-21 02:00 | 2 | 21 | 2 | 0% | 48.37%
2024-02-21 03:00 | 2 | 21 | 3 | 0% | 42.56%
2024-02-21 04:00 | 2 | 21 | 4 | 0% | 41.32%
2024-02-21 05:00 | 2 | 21 | 5 | 0% | 40.48%
2024-02-21 06:00 | 2 | 21 | 6 | 0% | 39.69%
2024-02-21 07:00 | 2 | 21 | 7 | 0% | 42.65%
2024-02-21 08:00 | 2 | 21 | 8 | 2.736% | 37.7%
2024-02-21 09:00 | 2 | 21 | 9 | 16.72% | 36.29%
2024-02-21 10:00 | 2 | 21 | 10 | 35.14% | 34.98%
2024-02-21 11:00 | 2 | 21 | 11 | 42.97% | 34.15%
2024-02-21 12:00 | 2 | 21 | 12 | 45.54% | 32.9%
2024-02-21 13:00 | 2 | 21 | 13 | 37.18% | 31.41%
2024-02-21 14:00 | 2 | 21 | 14 | 20.45% | 30.44%
2024-02-21 15:00 | 2 | 21 | 15 | 4.71% | 30.31%
2024-02-21 16:00 | 2 | 21 | 16 | 0.8923% | 30.54%
2024-02-21 17:00 | 2 | 21 | 17 | 0% | 31.55%
2024-02-21 18:00 | 2 | 21 | 18 | 0% | 32.29%
2024-02-21 19:00 | 2 | 21 | 19 | 0% | 33.42%
2024-02-21 20:00 | 2 | 21 | 20 | 0% | 34.23%
2024-02-21 21:00 | 2 | 21 | 21 | 0% | 34.67%
2024-02-21 22:00 | 2 | 21 | 22 | 0% | 35.17%
2024-02-21 23:00 | 2 | 21 | 23 | 0% | 36.67%
2024-02-22 | 2 | 22 | 0 | 0% | 44.25%
2024-02-22 01:00 | 2 | 22 | 1 | 0% | 35.73%
2024-02-22 02:00 | 2 | 22 | 2 | 0% | 35.92%
2024-02-22 03:00 | 2 | 22 | 3 | 0% | 35.96%
2024-02-22 04:00 | 2 | 22 | 4 | 0% | 35.97%
2024-02-22 05:00 | 2 | 22 | 5 | 0% | 31.88%
2024-02-22 06:00 | 2 | 22 | 6 | 0% | 36.53%
2024-02-22 07:00 | 2 | 22 | 7 | 0% | 36.48%
2024-02-22 08:00 | 2 | 22 | 8 | 0.2972% | 35.63%
2024-02-22 09:00 | 2 | 22 | 9 | 2.764% | 34.28%
2024-02-22 10:00 | 2 | 22 | 10 | 2.726% | 33.23%
2024-02-22 11:00 | 2 | 22 | 11 | 3.794% | 32.38%
2024-02-22 12:00 | 2 | 22 | 12 | 9.366% | 31.69%
2024-02-22 13:00 | 2 | 22 | 13 | 9.917% | 31.64%
2024-02-22 14:00 | 2 | 22 | 14 | 15.33% | 27.15%
2024-02-22 15:00 | 2 | 22 | 15 | 10.82% | 33.46%
2024-02-22 16:00 | 2 | 22 | 16 | 2.267% | 35.12%
2024-02-22 17:00 | 2 | 22 | 17 | 0% | 32.59%
2024-02-22 18:00 | 2 | 22 | 18 | 0% | 38.7%
2024-02-22 19:00 | 2 | 22 | 19 | 0% | 40.52%
2024-02-22 20:00 | 2 | 22 | 20 | 0% | 41.34%
2024-02-22 21:00 | 2 | 22 | 21 | 0% | 41.64%
2024-02-22 22:00 | 2 | 22 | 22 | 0% | 41.79%
2024-02-22 23:00 | 2 | 22 | 23 | 0% | 38.23%
2024-02-23 | 2 | 23 | 0 | 0% | 45.12%
2024-02-23 01:00 | 2 | 23 | 1 | 0% | 44.25%
2024-02-23 02:00 | 2 | 23 | 2 | 0% | 45.02%
2024-02-23 03:00 | 2 | 23 | 3 | 0% | 45.03%
2024-02-23 04:00 | 2 | 23 | 4 | 0% | 44.87%
2024-02-23 05:00 | 2 | 23 | 5 | 0% | 48.07%
2024-02-23 06:00 | 2 | 23 | 6 | 0% | 44.31%
2024-02-23 07:00 | 2 | 23 | 7 | 0% | 43.89%
2024-02-23 08:00 | 2 | 23 | 8 | 1.692% | 42.71%
2024-02-23 09:00 | 2 | 23 | 9 | 5.323% | 41.42%
2024-02-23 10:00 | 2 | 23 | 10 | 8.493% | 40.18%
2024-02-23 11:00 | 2 | 23 | 11 | 20.18% | 39.05%
2024-02-23 12:00 | 2 | 23 | 12 | 22.65% | 38.24%
2024-02-23 13:00 | 2 | 23 | 13 | 19.69% | 37.93%
2024-02-23 14:00 | 2 | 23 | 14 | 14.52% | 37.07%
2024-02-23 15:00 | 2 | 23 | 15 | 18.05% | 37.23%
2024-02-23 16:00 | 2 | 23 | 16 | 6.649% | 37.88%
2024-02-23 17:00 | 2 | 23 | 17 | 0% | 39.26%
2024-02-23 18:00 | 2 | 23 | 18 | 0% | 40.74%
2024-02-23 19:00 | 2 | 23 | 19 | 0% | 42.08%
2024-02-23 20:00 | 2 | 23 | 20 | 0% | 42.92%
2024-02-23 21:00 | 2 | 23 | 21 | 0% | 42.71%
2024-02-23 22:00 | 2 | 23 | 22 | 0% | 43.19%
2024-02-23 23:00 | 2 | 23 | 23 | 0% | 43.43%
2024-02-24 | 2 | 24 | 0 | 0% | 41.38%
2024-02-24 01:00 | 2 | 24 | 1 | 0% | 45.83%
2024-02-24 02:00 | 2 | 24 | 2 | 0% | 45.87%
2024-02-24 03:00 | 2 | 24 | 3 | 0% | 45.91%
2024-02-24 04:00 | 2 | 24 | 4 | 0% | 45.62%
2024-02-24 05:00 | 2 | 24 | 5 | 0% | 45.02%
2024-02-24 06:00 | 2 | 24 | 6 | 0% | 45.05%
2024-02-24 07:00 | 2 | 24 | 7 | 0.4868% | 44.52%
2024-02-24 08:00 | 2 | 24 | 8 | 12.34% | 42.44%
2024-02-24 09:00 | 2 | 24 | 9 | 28.89% | 40.81%
2024-02-24 10:00 | 2 | 24 | 10 | 41.79% | 39.15%
2024-02-24 11:00 | 2 | 24 | 11 | 42.76% | 38.02%
2024-02-24 12:00 | 2 | 24 | 12 | 34.59% | 37.53%
2024-02-24 13:00 | 2 | 24 | 13 | 15.9% | 36.48%
2024-02-24 14:00 | 2 | 24 | 14 | 8.921% | 36.04%
2024-02-24 15:00 | 2 | 24 | 15 | 5.56% | 35.8%
2024-02-24 16:00 | 2 | 24 | 16 | 2.128% | 36.49%
2024-02-24 17:00 | 2 | 24 | 17 | 0% | 37.76%
2024-02-24 18:00 | 2 | 24 | 18 | 0% | 39.15%
2024-02-24 19:00 | 2 | 24 | 19 | 0% | 40.33%
2024-02-24 20:00 | 2 | 24 | 20 | 0% | 40.94%
2024-02-24 21:00 | 2 | 24 | 21 | 0% | 41.06%
2024-02-24 22:00 | 2 | 24 | 22 | 0% | 42.67%
2024-02-24 23:00 | 2 | 24 | 23 | 0% | 41.02%
2024-02-25 | 2 | 25 | 0 | 0% | 43.07%
2024-02-25 01:00 | 2 | 25 | 1 | 0% | 41.4%
2024-02-25 02:00 | 2 | 25 | 2 | 0% | 41.29%
2024-02-25 03:00 | 2 | 25 | 3 | 0% | 41.56%
2024-02-25 04:00 | 2 | 25 | 4 | 0% | 41.54%
2024-02-25 05:00 | 2 | 25 | 5 | 0% | 41.62%
2024-02-25 06:00 | 2 | 25 | 6 | 0% | 41.7%
2024-02-25 07:00 | 2 | 25 | 7 | 0% | 40.94%
2024-02-25 08:00 | 2 | 25 | 8 | 0.9875% | 39.49%
2024-02-25 09:00 | 2 | 25 | 9 | 3.76% | 37.61%
2024-02-25 10:00 | 2 | 25 | 10 | 5.105% | 36.62%
2024-02-25 11:00 | 2 | 25 | 11 | 4.624% | 36.44%
2024-02-25 12:00 | 2 | 25 | 12 | 7.214% | 36.23%
2024-02-25 13:00 | 2 | 25 | 13 | 6.964% | 35.49%
2024-02-25 14:00 | 2 | 25 | 14 | 9.276% | 35.02%
2024-02-25 15:00 | 2 | 25 | 15 | 7.368% | 35.03%
2024-02-25 16:00 | 2 | 25 | 16 | 1.444% | 36.4%
2024-02-25 17:00 | 2 | 25 | 17 | 0% | 39.42%
2024-02-25 18:00 | 2 | 25 | 18 | 0% | 42.37%
2024-02-25 19:00 | 2 | 25 | 19 | 0% | 43.72%
2024-02-25 20:00 | 2 | 25 | 20 | 0% | 44.87%
2024-02-25 21:00 | 2 | 25 | 21 | 0% | 45.43%
2024-02-25 22:00 | 2 | 25 | 22 | 0% | 44.7%
2024-02-25 23:00 | 2 | 25 | 23 | 0% | 40.82%
2024-02-26 | 2 | 26 | 0 | 0% | 31.38%
2024-02-26 01:00 | 2 | 26 | 1 | 0% | 41.7%
2024-02-26 02:00 | 2 | 26 | 2 | 0% | 40.23%
2024-02-26 03:00 | 2 | 26 | 3 | 0% | 38.88%
2024-02-26 04:00 | 2 | 26 | 4 | 0% | 40.05%
2024-02-26 05:00 | 2 | 26 | 5 | 0% | 36.62%
2024-02-26 06:00 | 2 | 26 | 6 | 0% | 35.81%
2024-02-26 07:00 | 2 | 26 | 7 | 0% | 34.37%
2024-02-26 08:00 | 2 | 26 | 8 | 5.174% | 31.61%
2024-02-26 09:00 | 2 | 26 | 9 | 11.65% | 28.85%
2024-02-26 10:00 | 2 | 26 | 10 | 17.38% | 26.07%
2024-02-26 11:00 | 2 | 26 | 11 | 34.6% | 24.2%
2024-02-26 12:00 | 2 | 26 | 12 | 33.24% | 23.01%
2024-02-26 13:00 | 2 | 26 | 13 | 29.17% | 22.83%
2024-02-26 14:00 | 2 | 26 | 14 | 25.57% | 23.25%
2024-02-26 15:00 | 2 | 26 | 15 | 8.328% | 23.39%
2024-02-26 16:00 | 2 | 26 | 16 | 3.823% | 24.71%
2024-02-26 17:00 | 2 | 26 | 17 | 0% | 27.29%
2024-02-26 18:00 | 2 | 26 | 18 | 0% | 29.77%
2024-02-26 19:00 | 2 | 26 | 19 | 0% | 31.35%
2024-02-26 20:00 | 2 | 26 | 20 | 0% | 31.85%
2024-02-26 21:00 | 2 | 26 | 21 | 0% | 31.85%
2024-02-26 22:00 | 2 | 26 | 22 | 0% | 31.38%
2024-02-26 23:00 | 2 | 26 | 23 | 0% | 31.08%
2024-02-27 | 2 | 27 | 0 | 0% | 31.46%
2024-02-27 01:00 | 2 | 27 | 1 | 0% | 31%
2024-02-27 02:00 | 2 | 27 | 2 | 0% | 30.92%
2024-02-27 03:00 | 2 | 27 | 3 | 0% | 30.79%
2024-02-27 04:00 | 2 | 27 | 4 | 0% | 30.85%
2024-02-27 05:00 | 2 | 27 | 5 | 0% | 30.5%
2024-02-27 06:00 | 2 | 27 | 6 | 0% | 30.59%
2024-02-27 07:00 | 2 | 27 | 7 | 1.265% | 30.34%
2024-02-27 08:00 | 2 | 27 | 8 | 15.35% | 29.23%
2024-02-27 09:00 | 2 | 27 | 9 | 32.74% | 27.82%
2024-02-27 10:00 | 2 | 27 | 10 | 44.96% | 26.6%
2024-02-27 11:00 | 2 | 27 | 11 | 52.17% | 25.27%
2024-02-27 12:00 | 2 | 27 | 12 | 54.19% | 24.73%
2024-02-27 13:00 | 2 | 27 | 13 | 50.88% | 24.3%
2024-02-27 14:00 | 2 | 27 | 14 | 41.81% | 25.8%
2024-02-27 15:00 | 2 | 27 | 15 | 21.53% | 24.51%
2024-02-27 16:00 | 2 | 27 | 16 | 3.788% | 25.94%
2024-02-27 17:00 | 2 | 27 | 17 | 0% | 28.67%
2024-02-27 18:00 | 2 | 27 | 18 | 0% | 30.32%
2024-02-27 19:00 | 2 | 27 | 19 | 0% | 31.36%
2024-02-27 20:00 | 2 | 27 | 20 | 0% | 31.63%
2024-02-27 21:00 | 2 | 27 | 21 | 0% | 31.74%
2024-02-27 22:00 | 2 | 27 | 22 | 0% | 31.66%
2024-02-27 23:00 | 2 | 27 | 23 | 0% | 31.52%
2024-02-28 | 2 | 28 | 0 | 0% | 34.72%
2024-02-28 01:00 | 2 | 28 | 1 | 0% | 31.52%
2024-02-28 02:00 | 2 | 28 | 2 | 0% | 31.54%
2024-02-28 03:00 | 2 | 28 | 3 | 0% | 31.79%
2024-02-28 04:00 | 2 | 28 | 4 | 0% | 32.03%
2024-02-28 05:00 | 2 | 28 | 5 | 0% | 31.03%
2024-02-28 06:00 | 2 | 28 | 6 | 0% | 32.35%
2024-02-28 07:00 | 2 | 28 | 7 | 0% | 32.5%
2024-02-28 08:00 | 2 | 28 | 8 | 2.561% | 31.15%
2024-02-28 09:00 | 2 | 28 | 9 | 7.561% | 28.86%
2024-02-28 10:00 | 2 | 28 | 10 | 5.652% | 27.73%
2024-02-28 11:00 | 2 | 28 | 11 | 9.303% | 27.55%
2024-02-28 12:00 | 2 | 28 | 12 | 10.61% | 27.6%
2024-02-28 13:00 | 2 | 28 | 13 | 9.862% | 27.4%
2024-02-28 14:00 | 2 | 28 | 14 | 37.22% | 27.03%
2024-02-28 15:00 | 2 | 28 | 15 | 19.12% | 26.82%
2024-02-28 16:00 | 2 | 28 | 16 | 8.156% | 27.81%
2024-02-28 17:00 | 2 | 28 | 17 | 0.1632% | 29.32%
2024-02-28 18:00 | 2 | 28 | 18 | 0% | 31.84%
2024-02-28 19:00 | 2 | 28 | 19 | 0% | 33.27%
2024-02-28 20:00 | 2 | 28 | 20 | 0% | 34.18%
2024-02-28 21:00 | 2 | 28 | 21 | 0% | 34.95%
2024-02-28 22:00 | 2 | 28 | 22 | 0% | 35.27%
2024-02-28 23:00 | 2 | 28 | 23 | 0% | 34.45%
2024-02-29 | 2 | 29 | 0 | 0% | 48.07%
2024-02-29 01:00 | 2 | 29 | 1 | 0% | 29.57%
2024-02-29 02:00 | 2 | 29 | 2 | 0% | 29.25%
2024-02-29 03:00 | 2 | 29 | 3 | 0% | 28.91%
2024-02-29 04:00 | 2 | 29 | 4 | 0% | 28.86%
2024-02-29 05:00 | 2 | 29 | 5 | 0% | 30.28%
2024-02-29 06:00 | 2 | 29 | 6 | 0% | 31.2%
2024-02-29 07:00 | 2 | 29 | 7 | 0% | 48.21%
2024-02-29 08:00 | 2 | 29 | 8 | 0% | 49.54%
2024-02-29 09:00 | 2 | 29 | 9 | 0% | 34.67%
2024-02-29 10:00 | 2 | 29 | 10 | 0% | 54.03%
2024-02-29 11:00 | 2 | 29 | 11 | 0% | 38.19%
2024-02-29 12:00 | 2 | 29 | 12 | 0% | 39.7%
2024-02-29 13:00 | 2 | 29 | 13 | 0% | 41.51%
2024-02-29 14:00 | 2 | 29 | 14 | 0% | 42.41%
2024-02-29 15:00 | 2 | 29 | 15 | 0% | 43.79%
2024-02-29 16:00 | 2 | 29 | 16 | 0% | 45.32%
2024-02-29 17:00 | 2 | 29 | 17 | 0% | 47.21%
2024-02-29 18:00 | 2 | 29 | 18 | 0% | 48.47%
2024-02-29 19:00 | 2 | 29 | 19 | 0% | 49.01%
2024-02-29 20:00 | 2 | 29 | 20 | 0% | 48.74%
2024-02-29 21:00 | 2 | 29 | 21 | 0% | 48.4%
2024-02-29 22:00 | 2 | 29 | 22 | 0% | 48.65%
2024-02-29 23:00 | 2 | 29 | 23 | 0% | 48.09%
2024-03-01 | 3 | 1 | 0 | 0% | 39.03%
2024-03-01 01:00 | 3 | 1 | 1 | 0% | 39.73%
2024-03-01 02:00 | 3 | 1 | 2 | 0% | 39.75%
2024-03-01 03:00 | 3 | 1 | 3 | 0% | 40.21%
2024-03-01 04:00 | 3 | 1 | 4 | 0% | 40.6%
2024-03-01 05:00 | 3 | 1 | 5 | 0% | 40.78%
2024-03-01 06:00 | 3 | 1 | 6 | 0% | 40.31%
2024-03-01 07:00 | 3 | 1 | 7 | 0% | 39.37%
2024-03-01 08:00 | 3 | 1 | 8 | 0.7929% | 36.82%
2024-03-01 09:00 | 3 | 1 | 9 | 2.034% | 34.19%
2024-03-01 10:00 | 3 | 1 | 10 | 6.407% | 31.93%
2024-03-01 11:00 | 3 | 1 | 11 | 3.883% | 30.96%
2024-03-01 12:00 | 3 | 1 | 12 | 3.882% | 30.74%
2024-03-01 13:00 | 3 | 1 | 13 | 4.605% | 31.11%
2024-03-01 14:00 | 3 | 1 | 14 | 11.6% | 31.57%
2024-03-01 15:00 | 3 | 1 | 15 | 6.124% | 32.38%
2024-03-01 16:00 | 3 | 1 | 16 | 2.536% | 33.79%
2024-03-01 17:00 | 3 | 1 | 17 | 0% | 35.79%
2024-03-01 18:00 | 3 | 1 | 18 | 0% | 37.98%
2024-03-01 19:00 | 3 | 1 | 19 | 0% | 39.78%
2024-03-01 20:00 | 3 | 1 | 20 | 0% | 40.18%
2024-03-01 21:00 | 3 | 1 | 21 | 0% | 39.59%
2024-03-01 22:00 | 3 | 1 | 22 | 0% | 38.89%
2024-03-01 23:00 | 3 | 1 | 23 | 0% | 38.5%
2024-03-02 | 3 | 2 | 0 | 0% | 33.26%
2024-03-02 01:00 | 3 | 2 | 1 | 0% | 38.56%
2024-03-02 02:00 | 3 | 2 | 2 | 0% | 38.42%
2024-03-02 03:00 | 3 | 2 | 3 | 0% | 38.38%
2024-03-02 04:00 | 3 | 2 | 4 | 0% | 38.6%
2024-03-02 05:00 | 3 | 2 | 5 | 0% | 37.21%
2024-03-02 06:00 | 3 | 2 | 6 | 0% | 37.79%
2024-03-02 07:00 | 3 | 2 | 7 | 2.338% | 36.31%
2024-03-02 08:00 | 3 | 2 | 8 | 18.93% | 34.87%
2024-03-02 09:00 | 3 | 2 | 9 | 36.92% | 33.66%
2024-03-02 10:00 | 3 | 2 | 10 | 50.81% | 32.16%
2024-03-02 11:00 | 3 | 2 | 11 | 58.54% | 31.67%
2024-03-02 12:00 | 3 | 2 | 12 | 60.95% | 31.37%
2024-03-02 13:00 | 3 | 2 | 13 | 57.13% | 31.55%
2024-03-02 14:00 | 3 | 2 | 14 | 48.01% | 31.89%
2024-03-02 15:00 | 3 | 2 | 15 | 33.06% | 32.23%
2024-03-02 16:00 | 3 | 2 | 16 | 13.76% | 32.86%
2024-03-02 17:00 | 3 | 2 | 17 | 0.532% | 34.19%
2024-03-02 18:00 | 3 | 2 | 18 | 0% | 38.05%
2024-03-02 19:00 | 3 | 2 | 19 | 0% | 36.51%
2024-03-02 20:00 | 3 | 2 | 20 | 0% | 35.49%
2024-03-02 21:00 | 3 | 2 | 21 | 0% | 37.81%
2024-03-02 22:00 | 3 | 2 | 22 | 0% | 34.21%
2024-03-02 23:00 | 3 | 2 | 23 | 0% | 33.75%
2024-03-03 | 3 | 3 | 0 | 0% | 34.86%
2024-03-03 01:00 | 3 | 3 | 1 | 0% | 33.15%
2024-03-03 02:00 | 3 | 3 | 2 | 0% | 33.55%
2024-03-03 03:00 | 3 | 3 | 3 | 0% | 33.8%
2024-03-03 04:00 | 3 | 3 | 4 | 0% | 34.28%
2024-03-03 05:00 | 3 | 3 | 5 | 0% | 35.02%
2024-03-03 06:00 | 3 | 3 | 6 | 0% | 36.02%
2024-03-03 07:00 | 3 | 3 | 7 | 2.675% | 36.56%
2024-03-03 08:00 | 3 | 3 | 8 | 19.4% | 35.96%
2024-03-03 09:00 | 3 | 3 | 9 | 37.35% | 35.05%
2024-03-03 10:00 | 3 | 3 | 10 | 51.38% | 33.77%
2024-03-03 11:00 | 3 | 3 | 11 | 59.8% | 33.99%
2024-03-03 12:00 | 3 | 3 | 12 | 62.14% | 35.03%
2024-03-03 13:00 | 3 | 3 | 13 | 58.73% | 36.08%
2024-03-03 14:00 | 3 | 3 | 14 | 49.3% | 36.67%
2024-03-03 15:00 | 3 | 3 | 15 | 34.25% | 36.93%
2024-03-03 16:00 | 3 | 3 | 16 | 14.65% | 37.46%
2024-03-03 17:00 | 3 | 3 | 17 | 0.6812% | 38.51%
2024-03-03 18:00 | 3 | 3 | 18 | 0% | 39.04%
2024-03-03 19:00 | 3 | 3 | 19 | 0% | 39.24%
2024-03-03 20:00 | 3 | 3 | 20 | 0% | 38.6%
2024-03-03 21:00 | 3 | 3 | 21 | 0% | 37.66%
2024-03-03 22:00 | 3 | 3 | 22 | 0% | 36.58%
2024-03-03 23:00 | 3 | 3 | 23 | 0% | 35.78%
2024-03-04 | 3 | 4 | 0 | 0% | 39.71%
2024-03-04 01:00 | 3 | 4 | 1 | 0% | 34.69%
2024-03-04 02:00 | 3 | 4 | 2 | 0% | 32.82%
2024-03-04 03:00 | 3 | 4 | 3 | 0% | 33.85%
2024-03-04 04:00 | 3 | 4 | 4 | 0% | 33.8%
2024-03-04 05:00 | 3 | 4 | 5 | 0% | 34%
2024-03-04 06:00 | 3 | 4 | 6 | 0% | 33.69%
2024-03-04 07:00 | 3 | 4 | 7 | 3.159% | 33.45%
2024-03-04 08:00 | 3 | 4 | 8 | 20.53% | 32.15%
2024-03-04 09:00 | 3 | 4 | 9 | 38.28% | 31.25%
2024-03-04 10:00 | 3 | 4 | 10 | 51.5% | 30.47%
2024-03-04 11:00 | 3 | 4 | 11 | 36.43% | 29.87%
2024-03-04 12:00 | 3 | 4 | 12 | 25.68% | 29.56%
2024-03-04 13:00 | 3 | 4 | 13 | 13.5% | 29.25%
2024-03-04 14:00 | 3 | 4 | 14 | 24.66% | 29.52%
2024-03-04 15:00 | 3 | 4 | 15 | 15.62% | 30.17%
2024-03-04 16:00 | 3 | 4 | 16 | 9.878% | 31.37%
2024-03-04 17:00 | 3 | 4 | 17 | 0.6301% | 32.93%
2024-03-04 18:00 | 3 | 4 | 18 | 0% | 34.85%
2024-03-04 19:00 | 3 | 4 | 19 | 0% | 36.6%
2024-03-04 20:00 | 3 | 4 | 20 | 0% | 39.7%
2024-03-04 21:00 | 3 | 4 | 21 | 0% | 40.52%
2024-03-04 22:00 | 3 | 4 | 22 | 0% | 39.36%
2024-03-04 23:00 | 3 | 4 | 23 | 0% | 39.44%
2024-03-05 | 3 | 5 | 0 | 0% | 39.47%
2024-03-05 01:00 | 3 | 5 | 1 | 0% | 39.78%
2024-03-05 02:00 | 3 | 5 | 2 | 0% | 39.76%
2024-03-05 03:00 | 3 | 5 | 3 | 0% | 39.6%
2024-03-05 04:00 | 3 | 5 | 4 | 0% | 39.78%
2024-03-05 05:00 | 3 | 5 | 5 | 0% | 39.98%
2024-03-05 06:00 | 3 | 5 | 6 | 0% | 40.45%
2024-03-05 07:00 | 3 | 5 | 7 | 3.817% | 40.49%
2024-03-05 08:00 | 3 | 5 | 8 | 22.33% | 39.02%
2024-03-05 09:00 | 3 | 5 | 9 | 40.69% | 37.2%
2024-03-05 10:00 | 3 | 5 | 10 | 48.86% | 36.1%
2024-03-05 11:00 | 3 | 5 | 11 | 62.89% | 35.7%
2024-03-05 12:00 | 3 | 5 | 12 | 58.23% | 36.31%
2024-03-05 13:00 | 3 | 5 | 13 | 33.02% | 36.24%
2024-03-05 14:00 | 3 | 5 | 14 | 51.41% | 36.53%
2024-03-05 15:00 | 3 | 5 | 15 | 23.85% | 36.15%
2024-03-05 16:00 | 3 | 5 | 16 | 11.36% | 35.84%
2024-03-05 17:00 | 3 | 5 | 17 | 0.4915% | 36.47%
2024-03-05 18:00 | 3 | 5 | 18 | 0% | 37.69%
2024-03-05 19:00 | 3 | 5 | 19 | 0% | 38.42%
2024-03-05 20:00 | 3 | 5 | 20 | 0% | 38.56%
2024-03-05 21:00 | 3 | 5 | 21 | 0% | 38.67%
2024-03-05 22:00 | 3 | 5 | 22 | 0% | 38.41%
2024-03-05 23:00 | 3 | 5 | 23 | 0% | 38.85%
2024-03-06 | 3 | 6 | 0 | 0% | 34.08%
2024-03-06 01:00 | 3 | 6 | 1 | 0% | 39.6%
2024-03-06 02:00 | 3 | 6 | 2 | 0% | 39.74%
2024-03-06 03:00 | 3 | 6 | 3 | 0% | 38.68%
2024-03-06 04:00 | 3 | 6 | 4 | 0% | 39.75%
2024-03-06 05:00 | 3 | 6 | 5 | 0% | 39.13%
2024-03-06 06:00 | 3 | 6 | 6 | 0% | 39.07%
2024-03-06 07:00 | 3 | 6 | 7 | 4.532% | 39.58%
2024-03-06 08:00 | 3 | 6 | 8 | 23.65% | 35.88%
2024-03-06 09:00 | 3 | 6 | 9 | 41.67% | 33.99%
2024-03-06 10:00 | 3 | 6 | 10 | 55.59% | 32.24%
2024-03-06 11:00 | 3 | 6 | 11 | 64.14% | 31.67%
2024-03-06 12:00 | 3 | 6 | 12 | 66.44% | 31.47%
2024-03-06 13:00 | 3 | 6 | 13 | 62.22% | 32.4%
2024-03-06 14:00 | 3 | 6 | 14 | 52.21% | 31.67%
2024-03-06 15:00 | 3 | 6 | 15 | 36.91% | 31.83%
2024-03-06 16:00 | 3 | 6 | 16 | 17.05% | 32.37%
2024-03-06 17:00 | 3 | 6 | 17 | 1.278% | 33.12%
2024-03-06 18:00 | 3 | 6 | 18 | 0% | 34.26%
2024-03-06 19:00 | 3 | 6 | 19 | 0% | 34.88%
2024-03-06 20:00 | 3 | 6 | 20 | 0% | 34.81%
2024-03-06 21:00 | 3 | 6 | 21 | 0% | 34.59%
2024-03-06 22:00 | 3 | 6 | 22 | 0% | 33.9%
2024-03-06 23:00 | 3 | 6 | 23 | 0% | 33.14%
2024-03-07 | 3 | 7 | 0 | 0% | 37.14%
2024-03-07 01:00 | 3 | 7 | 1 | 0% | 33.85%
2024-03-07 02:00 | 3 | 7 | 2 | 0% | 33.58%
2024-03-07 03:00 | 3 | 7 | 3 | 0% | 33.2%
2024-03-07 04:00 | 3 | 7 | 4 | 0% | 32.87%
2024-03-07 05:00 | 3 | 7 | 5 | 0% | 32.88%
2024-03-07 06:00 | 3 | 7 | 6 | 0% | 33.13%
2024-03-07 07:00 | 3 | 7 | 7 | 1.371% | 33.31%
2024-03-07 08:00 | 3 | 7 | 8 | 12.06% | 32.51%
2024-03-07 09:00 | 3 | 7 | 9 | 33.6% | 31.34%
2024-03-07 10:00 | 3 | 7 | 10 | 29.8% | 30.61%
2024-03-07 11:00 | 3 | 7 | 11 | 32.96% | 30.19%
2024-03-07 12:00 | 3 | 7 | 12 | 55.08% | 29.87%
2024-03-07 13:00 | 3 | 7 | 13 | 53.06% | 29.66%
2024-03-07 14:00 | 3 | 7 | 14 | 37.88% | 29.7%
2024-03-07 15:00 | 3 | 7 | 15 | 19.12% | 29.98%
2024-03-07 16:00 | 3 | 7 | 16 | 9.63% | 31.03%
2024-03-07 17:00 | 3 | 7 | 17 | 1.172% | 32.62%
2024-03-07 18:00 | 3 | 7 | 18 | 0% | 34.48%
2024-03-07 19:00 | 3 | 7 | 19 | 0% | 33.58%
2024-03-07 20:00 | 3 | 7 | 20 | 0% | 36.87%
2024-03-07 21:00 | 3 | 7 | 21 | 0% | 37.38%
2024-03-07 22:00 | 3 | 7 | 22 | 0% | 37.55%
2024-03-07 23:00 | 3 | 7 | 23 | 0% | 36.94%
2024-03-08 | 3 | 8 | 0 | 0% | 28.53%
2024-03-08 01:00 | 3 | 8 | 1 | 0% | 37.34%
2024-03-08 02:00 | 3 | 8 | 2 | 0% | 35.23%
2024-03-08 03:00 | 3 | 8 | 3 | 0% | 34.56%
2024-03-08 04:00 | 3 | 8 | 4 | 0% | 33.98%
2024-03-08 05:00 | 3 | 8 | 5 | 0% | 32.96%
2024-03-08 06:00 | 3 | 8 | 6 | 0% | 31.85%
2024-03-08 07:00 | 3 | 8 | 7 | 3.401% | 30.26%
2024-03-08 08:00 | 3 | 8 | 8 | 16.12% | 27.82%
2024-03-08 09:00 | 3 | 8 | 9 | 34.19% | 25.66%
2024-03-08 10:00 | 3 | 8 | 10 | 54.52% | 24.38%
2024-03-08 11:00 | 3 | 8 | 11 | 63.86% | 23.51%
2024-03-08 12:00 | 3 | 8 | 12 | 66.41% | 25.19%
2024-03-08 13:00 | 3 | 8 | 13 | 62.1% | 23.88%
2024-03-08 14:00 | 3 | 8 | 14 | 46.03% | 24.26%
2024-03-08 15:00 | 3 | 8 | 15 | 30.13% | 24.46%
2024-03-08 16:00 | 3 | 8 | 16 | 8.462% | 25.07%
2024-03-08 17:00 | 3 | 8 | 17 | 1.161% | 26.58%
2024-03-08 18:00 | 3 | 8 | 18 | 0% | 28.28%
2024-03-08 19:00 | 3 | 8 | 19 | 0% | 29.67%
2024-03-08 20:00 | 3 | 8 | 20 | 0% | 30.32%
2024-03-08 21:00 | 3 | 8 | 21 | 0% | 30.4%
2024-03-08 22:00 | 3 | 8 | 22 | 0% | 30.15%
2024-03-08 23:00 | 3 | 8 | 23 | 0% | 29.38%
2024-03-09 | 3 | 9 | 0 | 0% | 22.55%
2024-03-09 01:00 | 3 | 9 | 1 | 0% | 27.72%
2024-03-09 02:00 | 3 | 9 | 2 | 0% | 29.18%
2024-03-09 03:00 | 3 | 9 | 3 | 0% | 26.25%
2024-03-09 04:00 | 3 | 9 | 4 | 0% | 25.67%
2024-03-09 05:00 | 3 | 9 | 5 | 0% | 25.47%
2024-03-09 06:00 | 3 | 9 | 6 | 0% | 26.44%
2024-03-09 07:00 | 3 | 9 | 7 | 2.3% | 23.81%
2024-03-09 08:00 | 3 | 9 | 8 | 7.06% | 24.02%
2024-03-09 09:00 | 3 | 9 | 9 | 17.89% | 20.76%
2024-03-09 10:00 | 3 | 9 | 10 | 54.38% | 19.59%
2024-03-09 11:00 | 3 | 9 | 11 | 63.48% | 19.32%
2024-03-09 12:00 | 3 | 9 | 12 | 66% | 18.67%
2024-03-09 13:00 | 3 | 9 | 13 | 61.65% | 18.18%
2024-03-09 14:00 | 3 | 9 | 14 | 34.41% | 17.37%
2024-03-09 15:00 | 3 | 9 | 15 | 22.62% | 16.7%
2024-03-09 16:00 | 3 | 9 | 16 | 10.92% | 17.35%
2024-03-09 17:00 | 3 | 9 | 17 | 1.421% | 18.25%
2024-03-09 18:00 | 3 | 9 | 18 | 0% | 19.48%
2024-03-09 19:00 | 3 | 9 | 19 | 0% | 20.84%
2024-03-09 20:00 | 3 | 9 | 20 | 0% | 21.6%
2024-03-09 21:00 | 3 | 9 | 21 | 0% | 23.61%
2024-03-09 22:00 | 3 | 9 | 22 | 0% | 23.92%
2024-03-09 23:00 | 3 | 9 | 23 | 0% | 22.04%
2024-03-10 | 3 | 10 | 0 | 0% | 32.06%
2024-03-10 01:00 | 3 | 10 | 1 | 0% | 22.01%
2024-03-10 02:00 | 3 | 10 | 2 | 0% | 21.93%
2024-03-10 03:00 | 3 | 10 | 3 | 0% | 22.31%
2024-03-10 04:00 | 3 | 10 | 4 | 0% | 22.74%
2024-03-10 05:00 | 3 | 10 | 5 | 0% | 23.49%
2024-03-10 06:00 | 3 | 10 | 6 | 0% | 24.53%
2024-03-10 07:00 | 3 | 10 | 7 | 4.929% | 24.92%
2024-03-10 08:00 | 3 | 10 | 8 | 10.46% | 24.11%
2024-03-10 09:00 | 3 | 10 | 9 | 11.49% | 23.24%
2024-03-10 10:00 | 3 | 10 | 10 | 9.108% | 23.15%
2024-03-10 11:00 | 3 | 10 | 11 | 8.847% | 23.6%
2024-03-10 12:00 | 3 | 10 | 12 | 11.29% | 24.05%
2024-03-10 13:00 | 3 | 10 | 13 | 6.838% | 24.78%
2024-03-10 14:00 | 3 | 10 | 14 | 8.918% | 28.1%
2024-03-10 15:00 | 3 | 10 | 15 | 17.01% | 26.27%
2024-03-10 16:00 | 3 | 10 | 16 | 11.52% | 27.32%
2024-03-10 17:00 | 3 | 10 | 17 | 1.419% | 28.96%
2024-03-10 18:00 | 3 | 10 | 18 | 0% | 31.51%
2024-03-10 19:00 | 3 | 10 | 19 | 0% | 33.21%
2024-03-10 20:00 | 3 | 10 | 20 | 0% | 33.64%
2024-03-10 21:00 | 3 | 10 | 21 | 0% | 33.48%
2024-03-10 22:00 | 3 | 10 | 22 | 0% | 33.18%
2024-03-10 23:00 | 3 | 10 | 23 | 0% | 32.55%
2024-03-11 | 3 | 11 | 0 | 0% | 34.55%
2024-03-11 01:00 | 3 | 11 | 1 | 0% | 31.74%
2024-03-11 02:00 | 3 | 11 | 2 | 0% | 31.74%
2024-03-11 03:00 | 3 | 11 | 3 | 0% | 32.19%
2024-03-11 04:00 | 3 | 11 | 4 | 0% | 32.77%
2024-03-11 05:00 | 3 | 11 | 5 | 0% | 33.22%
2024-03-11 06:00 | 3 | 11 | 6 | 0% | 33.34%
2024-03-11 07:00 | 3 | 11 | 7 | 4.578% | 32.95%
2024-03-11 08:00 | 3 | 11 | 8 | 17.1% | 31.45%
2024-03-11 09:00 | 3 | 11 | 9 | 34.14% | 30.25%
2024-03-11 10:00 | 3 | 11 | 10 | 48.84% | 29.42%
2024-03-11 11:00 | 3 | 11 | 11 | 64.97% | 29.25%
2024-03-11 12:00 | 3 | 11 | 12 | 47.75% | 29.41%
2024-03-11 13:00 | 3 | 11 | 13 | 63.47% | 29.88%
2024-03-11 14:00 | 3 | 11 | 14 | 47.61% | 30%
2024-03-11 15:00 | 3 | 11 | 15 | 30.56% | 30.13%
2024-03-11 16:00 | 3 | 11 | 16 | 12.27% | 33.47%
2024-03-11 17:00 | 3 | 11 | 17 | 1.585% | 31.66%
2024-03-11 18:00 | 3 | 11 | 18 | 0% | 33.18%
2024-03-11 19:00 | 3 | 11 | 19 | 0% | 34.49%
2024-03-11 20:00 | 3 | 11 | 20 | 0% | 35.25%
2024-03-11 21:00 | 3 | 11 | 21 | 0% | 35.04%
2024-03-11 22:00 | 3 | 11 | 22 | 0% | 34.72%
2024-03-11 23:00 | 3 | 11 | 23 | 0% | 34.65%
2024-03-12 | 3 | 12 | 0 | 0% | 29.58%
2024-03-12 01:00 | 3 | 12 | 1 | 0% | 36.24%
2024-03-12 02:00 | 3 | 12 | 2 | 0% | 34.47%
2024-03-12 03:00 | 3 | 12 | 3 | 0% | 34.23%
2024-03-12 04:00 | 3 | 12 | 4 | 0% | 33.47%
2024-03-12 05:00 | 3 | 12 | 5 | 0% | 32.64%
2024-03-12 06:00 | 3 | 12 | 6 | 0% | 31.24%
2024-03-12 07:00 | 3 | 12 | 7 | 1.401% | 28.82%
2024-03-12 08:00 | 3 | 12 | 8 | 4.636% | 25.53%
2024-03-12 09:00 | 3 | 12 | 9 | 10.98% | 22.11%
2024-03-12 10:00 | 3 | 12 | 10 | 14.47% | 19.58%
2024-03-12 11:00 | 3 | 12 | 11 | 10.67% | 18.53%
2024-03-12 12:00 | 3 | 12 | 12 | 24.86% | 18.43%
2024-03-12 13:00 | 3 | 12 | 13 | 27.67% | 19.06%
2024-03-12 14:00 | 3 | 12 | 14 | 41.43% | 19.92%
2024-03-12 15:00 | 3 | 12 | 15 | 27.71% | 21.1%
2024-03-12 16:00 | 3 | 12 | 16 | 19.46% | 22.33%
2024-03-12 17:00 | 3 | 12 | 17 | 2.273% | 24.42%
2024-03-12 18:00 | 3 | 12 | 18 | 0% | 27.36%
2024-03-12 19:00 | 3 | 12 | 19 | 0% | 29.26%
2024-03-12 20:00 | 3 | 12 | 20 | 0% | 30.46%
2024-03-12 21:00 | 3 | 12 | 21 | 0% | 30.43%
2024-03-12 22:00 | 3 | 12 | 22 | 0% | 30.48%
2024-03-12 23:00 | 3 | 12 | 23 | 0% | 30.4%
2024-03-13 | 3 | 13 | 0 | 0% | 34.22%
2024-03-13 01:00 | 3 | 13 | 1 | 0% | 29.64%
2024-03-13 02:00 | 3 | 13 | 2 | 0% | 29.88%
2024-03-13 03:00 | 3 | 13 | 3 | 0% | 29.95%
2024-03-13 04:00 | 3 | 13 | 4 | 0% | 29.8%
2024-03-13 05:00 | 3 | 13 | 5 | 0% | 29.14%
2024-03-13 06:00 | 3 | 13 | 6 | 0% | 28.61%
2024-03-13 07:00 | 3 | 13 | 7 | 5.559% | 27.55%
2024-03-13 08:00 | 3 | 13 | 8 | 22.59% | 25.85%
2024-03-13 09:00 | 3 | 13 | 9 | 46.11% | 24.22%
2024-03-13 10:00 | 3 | 13 | 10 | 60.52% | 23.15%
2024-03-13 11:00 | 3 | 13 | 11 | 69.04% | 22.75%
2024-03-13 12:00 | 3 | 13 | 12 | 71.01% | 22.96%
2024-03-13 13:00 | 3 | 13 | 13 | 49.2% | 23.2%
2024-03-13 14:00 | 3 | 13 | 14 | 44.12% | 24.25%
2024-03-13 15:00 | 3 | 13 | 15 | 14.26% | 25.28%
2024-03-13 16:00 | 3 | 13 | 16 | 11.28% | 26.72%
2024-03-13 17:00 | 3 | 13 | 17 | 1.425% | 29.19%
2024-03-13 18:00 | 3 | 13 | 18 | 0% | 31.85%
2024-03-13 19:00 | 3 | 13 | 19 | 0% | 34.15%
2024-03-13 20:00 | 3 | 13 | 20 | 0% | 35.11%
2024-03-13 21:00 | 3 | 13 | 21 | 0% | 35.63%
2024-03-13 22:00 | 3 | 13 | 22 | 0% | 35%
2024-03-13 23:00 | 3 | 13 | 23 | 0% | 34.49%
2024-03-14 | 3 | 14 | 0 | 0% | 34.45%
2024-03-14 01:00 | 3 | 14 | 1 | 0% | 33.64%
2024-03-14 02:00 | 3 | 14 | 2 | 0% | 33.07%
2024-03-14 03:00 | 3 | 14 | 3 | 0% | 32.31%
2024-03-14 04:00 | 3 | 14 | 4 | 0% | 31.56%
2024-03-14 05:00 | 3 | 14 | 5 | 0% | 30.95%
2024-03-14 06:00 | 3 | 14 | 6 | 0% | 30.49%
2024-03-14 07:00 | 3 | 14 | 7 | 4.217% | 29.38%
2024-03-14 08:00 | 3 | 14 | 8 | 9.909% | 27.01%
2024-03-14 09:00 | 3 | 14 | 9 | 24.43% | 24.89%
2024-03-14 10:00 | 3 | 14 | 10 | 27.21% | 23.48%
2024-03-14 11:00 | 3 | 14 | 11 | 58.11% | 24.17%
2024-03-14 12:00 | 3 | 14 | 12 | 72.94% | 23.26%
2024-03-14 13:00 | 3 | 14 | 13 | 59.17% | 23.39%
2024-03-14 14:00 | 3 | 14 | 14 | 50.83% | 23.91%
2024-03-14 15:00 | 3 | 14 | 15 | 10.59% | 24.71%
2024-03-14 16:00 | 3 | 14 | 16 | 8.813% | 25.65%
2024-03-14 17:00 | 3 | 14 | 17 | 2.53% | 27.34%
2024-03-14 18:00 | 3 | 14 | 18 | 0% | 30.16%
2024-03-14 19:00 | 3 | 14 | 19 | 0% | 32.44%
2024-03-14 20:00 | 3 | 14 | 20 | 0% | 33.68%
2024-03-14 21:00 | 3 | 14 | 21 | 0% | 34.38%
2024-03-14 22:00 | 3 | 14 | 22 | 0% | 34.41%
2024-03-14 23:00 | 3 | 14 | 23 | 0% | 33.94%
2024-03-15 | 3 | 15 | 0 | 0% | 36.35%
2024-03-15 01:00 | 3 | 15 | 1 | 0% | 34.34%
2024-03-15 02:00 | 3 | 15 | 2 | 0% | 34.75%
2024-03-15 03:00 | 3 | 15 | 3 | 0% | 34.65%
2024-03-15 04:00 | 3 | 15 | 4 | 0% | 35.31%
2024-03-15 05:00 | 3 | 15 | 5 | 0% | 35.92%
2024-03-15 06:00 | 3 | 15 | 6 | 0% | 36.62%
2024-03-15 07:00 | 3 | 15 | 7 | 9.788% | 35.79%
2024-03-15 08:00 | 3 | 15 | 8 | 29.98% | 34.1%
2024-03-15 09:00 | 3 | 15 | 9 | 49.35% | 32.26%
2024-03-15 10:00 | 3 | 15 | 10 | 64.02% | 32.4%
2024-03-15 11:00 | 3 | 15 | 11 | 72.27% | 33.46%
2024-03-15 12:00 | 3 | 15 | 12 | 74.4% | 34.53%
2024-03-15 13:00 | 3 | 15 | 13 | 69.84% | 38.72%
2024-03-15 14:00 | 3 | 15 | 14 | 59.8% | 36.19%
2024-03-15 15:00 | 3 | 15 | 15 | 43.89% | 36.63%
2024-03-15 16:00 | 3 | 15 | 16 | 22.36% | 36.69%
2024-03-15 17:00 | 3 | 15 | 17 | 3.39% | 37.3%
2024-03-15 18:00 | 3 | 15 | 18 | 0% | 39.17%
2024-03-15 19:00 | 3 | 15 | 19 | 0% | 40.09%
2024-03-15 20:00 | 3 | 15 | 20 | 0% | 40.39%
2024-03-15 21:00 | 3 | 15 | 21 | 0% | 39.6%
2024-03-15 22:00 | 3 | 15 | 22 | 0% | 38.74%
2024-03-15 23:00 | 3 | 15 | 23 | 0% | 37.59%
2024-03-16 | 3 | 16 | 0 | 0% | 42.53%
2024-03-16 01:00 | 3 | 16 | 1 | 0% | 34.81%
2024-03-16 02:00 | 3 | 16 | 2 | 0% | 33.2%
2024-03-16 03:00 | 3 | 16 | 3 | 0% | 31.71%
2024-03-16 04:00 | 3 | 16 | 4 | 0% | 30.17%
2024-03-16 05:00 | 3 | 16 | 5 | 0% | 28.95%
2024-03-16 06:00 | 3 | 16 | 6 | 0% | 28.42%
2024-03-16 07:00 | 3 | 16 | 7 | 10.11% | 27.09%
2024-03-16 08:00 | 3 | 16 | 8 | 30.64% | 24.46%
2024-03-16 09:00 | 3 | 16 | 9 | 50.02% | 22.85%
2024-03-16 10:00 | 3 | 16 | 10 | 64.78% | 22.46%
2024-03-16 11:00 | 3 | 16 | 11 | 58.65% | 22.48%
2024-03-16 12:00 | 3 | 16 | 12 | 55.31% | 23.33%
2024-03-16 13:00 | 3 | 16 | 13 | 31.94% | 24.16%
2024-03-16 14:00 | 3 | 16 | 14 | 23.31% | 25.76%
2024-03-16 15:00 | 3 | 16 | 15 | 15.23% | 27.27%
2024-03-16 16:00 | 3 | 16 | 16 | 10.88% | 28%
2024-03-16 17:00 | 3 | 16 | 17 | 1.522% | 29.78%
2024-03-16 18:00 | 3 | 16 | 18 | 0% | 33.25%
2024-03-16 19:00 | 3 | 16 | 19 | 0% | 36.15%
2024-03-16 20:00 | 3 | 16 | 20 | 0% | 38.32%
2024-03-16 21:00 | 3 | 16 | 21 | 0% | 40.11%
2024-03-16 22:00 | 3 | 16 | 22 | 0% | 41.13%
2024-03-16 23:00 | 3 | 16 | 23 | 0% | 41.04%
2024-03-17 | 3 | 17 | 0 | 0% | 41.14%
2024-03-17 01:00 | 3 | 17 | 1 | 0% | 42.53%
2024-03-17 02:00 | 3 | 17 | 2 | 0% | 43.1%
2024-03-17 03:00 | 3 | 17 | 3 | 0% | 43.41%
2024-03-17 04:00 | 3 | 17 | 4 | 0% | 43.85%
2024-03-17 05:00 | 3 | 17 | 5 | 0% | 44.22%
2024-03-17 06:00 | 3 | 17 | 6 | 0% | 44.59%
2024-03-17 07:00 | 3 | 17 | 7 | 7.192% | 43.61%
2024-03-17 08:00 | 3 | 17 | 8 | 15.03% | 41.35%
2024-03-17 09:00 | 3 | 17 | 9 | 9% | 40.36%
2024-03-17 10:00 | 3 | 17 | 10 | 12.02% | 40.5%
2024-03-17 11:00 | 3 | 17 | 11 | 14.95% | 41.69%
2024-03-17 12:00 | 3 | 17 | 12 | 12.82% | 43.13%
2024-03-17 13:00 | 3 | 17 | 13 | 17.57% | 43.88%
2024-03-17 14:00 | 3 | 17 | 14 | 17.47% | 44.29%
2024-03-17 15:00 | 3 | 17 | 15 | 11.39% | 44.02%
2024-03-17 16:00 | 3 | 17 | 16 | 6.342% | 44.25%
2024-03-17 17:00 | 3 | 17 | 17 | 1.602% | 45.11%
2024-03-17 18:00 | 3 | 17 | 18 | 0% | 46.42%
2024-03-17 19:00 | 3 | 17 | 19 | 0% | 47.13%
2024-03-17 20:00 | 3 | 17 | 20 | 0% | 45.77%
2024-03-17 21:00 | 3 | 17 | 21 | 0% | 46.14%
2024-03-17 22:00 | 3 | 17 | 22 | 0% | 44.32%
2024-03-17 23:00 | 3 | 17 | 23 | 0% | 42.48%
2024-03-18 | 3 | 18 | 0 | 0% | 30.96%
2024-03-18 01:00 | 3 | 18 | 1 | 0% | 39.34%
2024-03-18 02:00 | 3 | 18 | 2 | 0% | 37.21%
2024-03-18 03:00 | 3 | 18 | 3 | 0% | 35.58%
2024-03-18 04:00 | 3 | 18 | 4 | 0% | 34.76%
2024-03-18 05:00 | 3 | 18 | 5 | 0% | 32.48%
2024-03-18 06:00 | 3 | 18 | 6 | 0% | 31.32%
2024-03-18 07:00 | 3 | 18 | 7 | 1.023% | 29.56%
2024-03-18 08:00 | 3 | 18 | 8 | 4.207% | 26.9%
2024-03-18 09:00 | 3 | 18 | 9 | 11.27% | 24.83%
2024-03-18 10:00 | 3 | 18 | 10 | 13.9% | 23.48%
2024-03-18 11:00 | 3 | 18 | 11 | 19.13% | 23.06%
2024-03-18 12:00 | 3 | 18 | 12 | 19.69% | 22.92%
2024-03-18 13:00 | 3 | 18 | 13 | 22.55% | 23.87%
2024-03-18 14:00 | 3 | 18 | 14 | 11.97% | 24.99%
2024-03-18 15:00 | 3 | 18 | 15 | 8.304% | 26.06%
2024-03-18 16:00 | 3 | 18 | 16 | 4.573% | 26.41%
2024-03-18 17:00 | 3 | 18 | 17 | 0.8624% | 22.94%
2024-03-18 18:00 | 3 | 18 | 18 | 0% | 28.64%
2024-03-18 19:00 | 3 | 18 | 19 | 0% | 30.28%
2024-03-18 20:00 | 3 | 18 | 20 | 0% | 31.47%
2024-03-18 21:00 | 3 | 18 | 21 | 0% | 32.14%
2024-03-18 22:00 | 3 | 18 | 22 | 0% | 32%
2024-03-18 23:00 | 3 | 18 | 23 | 0% | 31.57%
2024-03-19 | 3 | 19 | 0 | 0% | 30.01%
2024-03-19 01:00 | 3 | 19 | 1 | 0% | 30.23%
2024-03-19 02:00 | 3 | 19 | 2 | 0% | 29.69%
2024-03-19 03:00 | 3 | 19 | 3 | 0% | 29.03%
2024-03-19 04:00 | 3 | 19 | 4 | 0% | 28.88%
2024-03-19 05:00 | 3 | 19 | 5 | 0% | 29.05%
2024-03-19 06:00 | 3 | 19 | 6 | 0% | 29.07%
2024-03-19 07:00 | 3 | 19 | 7 | 1.19% | 27.81%
2024-03-19 08:00 | 3 | 19 | 8 | 3.334% | 24.42%
2024-03-19 09:00 | 3 | 19 | 9 | 6.092% | 21.63%
2024-03-19 10:00 | 3 | 19 | 10 | 5.882% | 20.24%
2024-03-19 11:00 | 3 | 19 | 11 | 37.24% | 19.99%
2024-03-19 12:00 | 3 | 19 | 12 | 19.83% | 19.96%
2024-03-19 13:00 | 3 | 19 | 13 | 12.91% | 19.93%
2024-03-19 14:00 | 3 | 19 | 14 | 19.25% | 20.52%
2024-03-19 15:00 | 3 | 19 | 15 | 11.63% | 20.12%
2024-03-19 16:00 | 3 | 19 | 16 | 12.36% | 20.14%
2024-03-19 17:00 | 3 | 19 | 17 | 2.677% | 21.55%
2024-03-19 18:00 | 3 | 19 | 18 | 0% | 24.09%
2024-03-19 19:00 | 3 | 19 | 19 | 0% | 26.57%
2024-03-19 20:00 | 3 | 19 | 20 | 0% | 28.34%
2024-03-19 21:00 | 3 | 19 | 21 | 0% | 29.75%
2024-03-19 22:00 | 3 | 19 | 22 | 0% | 29.98%
2024-03-19 23:00 | 3 | 19 | 23 | 0% | 29.88%
2024-03-20 | 3 | 20 | 0 | 0% | 27.26%
2024-03-20 01:00 | 3 | 20 | 1 | 0% | 29.93%
2024-03-20 02:00 | 3 | 20 | 2 | 0% | 30.01%
2024-03-20 03:00 | 3 | 20 | 3 | 0% | 29.76%
2024-03-20 04:00 | 3 | 20 | 4 | 0% | 29.52%
2024-03-20 05:00 | 3 | 20 | 5 | 0% | 30.91%
2024-03-20 06:00 | 3 | 20 | 6 | 0% | 29.13%
2024-03-20 07:00 | 3 | 20 | 7 | 4.213% | 27.95%
2024-03-20 08:00 | 3 | 20 | 8 | 12.27% | 25.24%
2024-03-20 09:00 | 3 | 20 | 9 | 18.94% | 22.9%
2024-03-20 10:00 | 3 | 20 | 10 | 21.86% | 21.69%
2024-03-20 11:00 | 3 | 20 | 11 | 23.44% | 21.11%
2024-03-20 12:00 | 3 | 20 | 12 | 18.82% | 20.73%
2024-03-20 13:00 | 3 | 20 | 13 | 18.11% | 20.63%
2024-03-20 14:00 | 3 | 20 | 14 | 15.56% | 20.49%
2024-03-20 15:00 | 3 | 20 | 15 | 10.82% | 20.45%
2024-03-20 16:00 | 3 | 20 | 16 | 7.112% | 20.37%
2024-03-20 17:00 | 3 | 20 | 17 | 2.967% | 20.97%
2024-03-20 18:00 | 3 | 20 | 18 | 0% | 23.06%
2024-03-20 19:00 | 3 | 20 | 19 | 0% | 25.54%
2024-03-20 20:00 | 3 | 20 | 20 | 0% | 25.77%
2024-03-20 21:00 | 3 | 20 | 21 | 0% | 26.75%
2024-03-20 22:00 | 3 | 20 | 22 | 0% | 26.78%
2024-03-20 23:00 | 3 | 20 | 23 | 0% | 27.57%
2024-03-21 | 3 | 21 | 0 | 0% | 31.02%
2024-03-21 01:00 | 3 | 21 | 1 | 0% | 28.91%
2024-03-21 02:00 | 3 | 21 | 2 | 0% | 30.4%
2024-03-21 03:00 | 3 | 21 | 3 | 0% | 31.63%
2024-03-21 04:00 | 3 | 21 | 4 | 0% | 32.82%
2024-03-21 05:00 | 3 | 21 | 5 | 0% | 33.84%
2024-03-21 06:00 | 3 | 21 | 6 | 0.3737% | 33.51%
2024-03-21 07:00 | 3 | 21 | 7 | 8.899% | 32.24%
2024-03-21 08:00 | 3 | 21 | 8 | 20.58% | 29.65%
2024-03-21 09:00 | 3 | 21 | 9 | 39.88% | 27.34%
2024-03-21 10:00 | 3 | 21 | 10 | 44.3% | 26.4%
2024-03-21 11:00 | 3 | 21 | 11 | 72.88% | 26.57%
2024-03-21 12:00 | 3 | 21 | 12 | 54.26% | 26.58%
2024-03-21 13:00 | 3 | 21 | 13 | 69.29% | 26.83%
2024-03-21 14:00 | 3 | 21 | 14 | 58.89% | 26.54%
2024-03-21 15:00 | 3 | 21 | 15 | 36.21% | 25.81%
2024-03-21 16:00 | 3 | 21 | 16 | 18.95% | 25.05%
2024-03-21 17:00 | 3 | 21 | 17 | 5.329% | 25.59%
2024-03-21 18:00 | 3 | 21 | 18 | 0% | 27.87%
2024-03-21 19:00 | 3 | 21 | 19 | 0% | 32.99%
2024-03-21 20:00 | 3 | 21 | 20 | 0% | 32.44%
2024-03-21 21:00 | 3 | 21 | 21 | 0% | 33.01%
2024-03-21 22:00 | 3 | 21 | 22 | 0% | 32.54%
2024-03-21 23:00 | 3 | 21 | 23 | 0% | 31.76%
2024-03-22 | 3 | 22 | 0 | 0% | 44.7%
2024-03-22 01:00 | 3 | 22 | 1 | 0% | 30.4%
2024-03-22 02:00 | 3 | 22 | 2 | 0% | 30.41%
2024-03-22 03:00 | 3 | 22 | 3 | 0% | 30.82%
2024-03-22 04:00 | 3 | 22 | 4 | 0% | 31.4%
2024-03-22 05:00 | 3 | 22 | 5 | 0% | 31.9%
2024-03-22 06:00 | 3 | 22 | 6 | 0.3862% | 32.16%
2024-03-22 07:00 | 3 | 22 | 7 | 5.798% | 31.98%
2024-03-22 08:00 | 3 | 22 | 8 | 8.16% | 30.71%
2024-03-22 09:00 | 3 | 22 | 9 | 14.45% | 28.46%
2024-03-22 10:00 | 3 | 22 | 10 | 19.89% | 30.11%
2024-03-22 11:00 | 3 | 22 | 11 | 21.35% | 31.19%
2024-03-22 12:00 | 3 | 22 | 12 | 23.32% | 33.14%
2024-03-22 13:00 | 3 | 22 | 13 | 13.5% | 34.86%
2024-03-22 14:00 | 3 | 22 | 14 | 9.231% | 36.6%
2024-03-22 15:00 | 3 | 22 | 15 | 9.549% | 38.15%
2024-03-22 16:00 | 3 | 22 | 16 | 4.576% | 41.21%
2024-03-22 17:00 | 3 | 22 | 17 | 1.952% | 41.39%
2024-03-22 18:00 | 3 | 22 | 18 | 0% | 44.24%
2024-03-22 19:00 | 3 | 22 | 19 | 0% | 46.46%
2024-03-22 20:00 | 3 | 22 | 20 | 0% | 47.68%
2024-03-22 21:00 | 3 | 22 | 21 | 0% | 47.99%
2024-03-22 22:00 | 3 | 22 | 22 | 0% | 49.09%
2024-03-22 23:00 | 3 | 22 | 23 | 0% | 46.3%
2024-03-23 | 3 | 23 | 0 | 0% | 42.32%
2024-03-23 01:00 | 3 | 23 | 1 | 0% | 43.99%
2024-03-23 02:00 | 3 | 23 | 2 | 0% | 40.7%
2024-03-23 03:00 | 3 | 23 | 3 | 0% | 42.58%
2024-03-23 04:00 | 3 | 23 | 4 | 0% | 41.29%
2024-03-23 05:00 | 3 | 23 | 5 | 0% | 43.08%
2024-03-23 06:00 | 3 | 23 | 6 | 0% | 39.29%
2024-03-23 07:00 | 3 | 23 | 7 | 1.555% | 37.46%
2024-03-23 08:00 | 3 | 23 | 8 | 6.17% | 34.84%
2024-03-23 09:00 | 3 | 23 | 9 | 8.881% | 33.11%
2024-03-23 10:00 | 3 | 23 | 10 | 14.73% | 32.76%
2024-03-23 11:00 | 3 | 23 | 11 | 19.29% | 32.95%
2024-03-23 12:00 | 3 | 23 | 12 | 23.04% | 33.61%
2024-03-23 13:00 | 3 | 23 | 13 | 23.56% | 34.61%
2024-03-23 14:00 | 3 | 23 | 14 | 39.07% | 35.52%
2024-03-23 15:00 | 3 | 23 | 15 | 44.64% | 34.64%
2024-03-23 16:00 | 3 | 23 | 16 | 24.16% | 37.66%
2024-03-23 17:00 | 3 | 23 | 17 | 5.784% | 39.46%
2024-03-23 18:00 | 3 | 23 | 18 | 0% | 42.31%
2024-03-23 19:00 | 3 | 23 | 19 | 0% | 44.28%
2024-03-23 20:00 | 3 | 23 | 20 | 0% | 45.16%
2024-03-23 21:00 | 3 | 23 | 21 | 0% | 45.17%
2024-03-23 22:00 | 3 | 23 | 22 | 0% | 44.41%
2024-03-23 23:00 | 3 | 23 | 23 | 0% | 43.38%
2024-03-24 | 3 | 24 | 0 | 0% | 42.95%
2024-03-24 01:00 | 3 | 24 | 1 | 0% | 41.18%
2024-03-24 02:00 | 3 | 24 | 2 | 0% | 39.82%
2024-03-24 03:00 | 3 | 24 | 3 | 0% | 38.55%
2024-03-24 04:00 | 3 | 24 | 4 | 0% | 37.44%
2024-03-24 05:00 | 3 | 24 | 5 | 0% | 36.71%
2024-03-24 06:00 | 3 | 24 | 6 | 0% | 35.34%
2024-03-24 07:00 | 3 | 24 | 7 | 3.435% | 33.35%
2024-03-24 08:00 | 3 | 24 | 8 | 6.653% | 30.48%
2024-03-24 09:00 | 3 | 24 | 9 | 14.72% | 28.32%
2024-03-24 10:00 | 3 | 24 | 10 | 22.99% | 27.47%
2024-03-24 11:00 | 3 | 24 | 11 | 20.28% | 28.25%
2024-03-24 12:00 | 3 | 24 | 12 | 20.71% | 29.94%
2024-03-24 13:00 | 3 | 24 | 13 | 62.45% | 31.22%
2024-03-24 14:00 | 3 | 24 | 14 | 48.08% | 32.75%
2024-03-24 15:00 | 3 | 24 | 15 | 10.56% | 34.17%
2024-03-24 16:00 | 3 | 24 | 16 | 9.497% | 36.24%
2024-03-24 17:00 | 3 | 24 | 17 | 2.738% | 38.6%
2024-03-24 18:00 | 3 | 24 | 18 | 0% | 39.36%
2024-03-24 19:00 | 3 | 24 | 19 | 0% | 43.88%
2024-03-24 20:00 | 3 | 24 | 20 | 0% | 45.04%
2024-03-24 21:00 | 3 | 24 | 21 | 0% | 45.25%
2024-03-24 22:00 | 3 | 24 | 22 | 0% | 44.31%
2024-03-24 23:00 | 3 | 24 | 23 | 0% | 43.12%
2024-03-25 | 3 | 25 | 0 | 0% | 34.34%
2024-03-25 01:00 | 3 | 25 | 1 | 0% | 41.62%
2024-03-25 02:00 | 3 | 25 | 2 | 0% | 40.99%
2024-03-25 03:00 | 3 | 25 | 3 | 0% | 40.63%
2024-03-25 04:00 | 3 | 25 | 4 | 0% | 39.88%
2024-03-25 05:00 | 3 | 25 | 5 | 0% | 39.29%
2024-03-25 06:00 | 3 | 25 | 6 | 0.2946% | 38.75%
2024-03-25 07:00 | 3 | 25 | 7 | 4.527% | 37.12%
2024-03-25 08:00 | 3 | 25 | 8 | 14.42% | 34.75%
2024-03-25 09:00 | 3 | 25 | 9 | 24.25% | 33.17%
2024-03-25 10:00 | 3 | 25 | 10 | 28.08% | 32.23%
2024-03-25 11:00 | 3 | 25 | 11 | 42.25% | 32.63%
2024-03-25 12:00 | 3 | 25 | 12 | 70.03% | 32.79%
2024-03-25 13:00 | 3 | 25 | 13 | 65.72% | 32.39%
2024-03-25 14:00 | 3 | 25 | 14 | 56.38% | 32.45%
2024-03-25 15:00 | 3 | 25 | 15 | 36.1% | 31.89%
2024-03-25 16:00 | 3 | 25 | 16 | 23.03% | 31.64%
2024-03-25 17:00 | 3 | 25 | 17 | 5.35% | 31.36%
2024-03-25 18:00 | 3 | 25 | 18 | 0% | 31.66%
2024-03-25 19:00 | 3 | 25 | 19 | 0% | 32.25%
2024-03-25 20:00 | 3 | 25 | 20 | 0% | 33.02%
2024-03-25 21:00 | 3 | 25 | 21 | 0% | 33.27%
2024-03-25 22:00 | 3 | 25 | 22 | 0% | 33.62%
2024-03-25 23:00 | 3 | 25 | 23 | 0% | 33.96%
2024-03-26 | 3 | 26 | 0 | 0% | 29.59%
2024-03-26 01:00 | 3 | 26 | 1 | 0% | 34.09%
2024-03-26 02:00 | 3 | 26 | 2 | 0% | 34.08%
2024-03-26 03:00 | 3 | 26 | 3 | 0% | 34.31%
2024-03-26 04:00 | 3 | 26 | 4 | 0% | 34.69%
2024-03-26 05:00 | 3 | 26 | 5 | 0% | 35.3%
2024-03-26 06:00 | 3 | 26 | 6 | 0.4611% | 35.53%
2024-03-26 07:00 | 3 | 26 | 7 | 7.383% | 34.9%
2024-03-26 08:00 | 3 | 26 | 8 | 30.23% | 32.98%
2024-03-26 09:00 | 3 | 26 | 9 | 46.51% | 32.07%
2024-03-26 10:00 | 3 | 26 | 10 | 36.94% | 31.85%
2024-03-26 11:00 | 3 | 26 | 11 | 49.24% | 31.63%
2024-03-26 12:00 | 3 | 26 | 12 | 66.57% | 30.83%
2024-03-26 13:00 | 3 | 26 | 13 | 47.3% | 30.15%
2024-03-26 14:00 | 3 | 26 | 14 | 27.1% | 29.35%
2024-03-26 15:00 | 3 | 26 | 15 | 11.25% | 27.84%
2024-03-26 16:00 | 3 | 26 | 16 | 4.475% | 26.07%
2024-03-26 17:00 | 3 | 26 | 17 | 1.374% | 25.38%
2024-03-26 18:00 | 3 | 26 | 18 | 0% | 26.13%
2024-03-26 19:00 | 3 | 26 | 19 | 0% | 27.62%
2024-03-26 20:00 | 3 | 26 | 20 | 0% | 28.24%
2024-03-26 21:00 | 3 | 26 | 21 | 0% | 29.02%
2024-03-26 22:00 | 3 | 26 | 22 | 0% | 29.79%
2024-03-26 23:00 | 3 | 26 | 23 | 0% | 29.41%
2024-03-27 | 3 | 27 | 0 | 0% | 37.3%
2024-03-27 01:00 | 3 | 27 | 1 | 0% | 29.73%
2024-03-27 02:00 | 3 | 27 | 2 | 0% | 30.44%
2024-03-27 03:00 | 3 | 27 | 3 | 0% | 31.24%
2024-03-27 04:00 | 3 | 27 | 4 | 0% | 32.14%
2024-03-27 05:00 | 3 | 27 | 5 | 0% | 32.86%
2024-03-27 06:00 | 3 | 27 | 6 | 0% | 33.36%
2024-03-27 07:00 | 3 | 27 | 7 | 1.021% | 32.34%
2024-03-27 08:00 | 3 | 27 | 8 | 2.423% | 29.99%
2024-03-27 09:00 | 3 | 27 | 9 | 4.491% | 28.97%
2024-03-27 10:00 | 3 | 27 | 10 | 7.162% | 29.04%
2024-03-27 11:00 | 3 | 27 | 11 | 8.985% | 29.94%
2024-03-27 12:00 | 3 | 27 | 12 | 11.52% | 31.34%
2024-03-27 13:00 | 3 | 27 | 13 | 13.96% | 32.61%
2024-03-27 14:00 | 3 | 27 | 14 | 12.27% | 33.88%
2024-03-27 15:00 | 3 | 27 | 15 | 12.21% | 37.45%
2024-03-27 16:00 | 3 | 27 | 16 | 6.845% | 35.33%
2024-03-27 17:00 | 3 | 27 | 17 | 2.679% | 36.12%
2024-03-27 18:00 | 3 | 27 | 18 | 0% | 37.2%
2024-03-27 19:00 | 3 | 27 | 19 | 0% | 38.34%
2024-03-27 20:00 | 3 | 27 | 20 | 0% | 38.59%
2024-03-27 21:00 | 3 | 27 | 21 | 0% | 38.36%
2024-03-27 22:00 | 3 | 27 | 22 | 0% | 33.27%
2024-03-27 23:00 | 3 | 27 | 23 | 0% | 37.84%
2024-03-28 | 3 | 28 | 0 | 0% | 43.68%
2024-03-28 01:00 | 3 | 28 | 1 | 0% | 37.56%
2024-03-28 02:00 | 3 | 28 | 2 | 0% | 38.95%
2024-03-28 03:00 | 3 | 28 | 3 | 0% | 39.92%
2024-03-28 04:00 | 3 | 28 | 4 | 0% | 40.92%
2024-03-28 05:00 | 3 | 28 | 5 | 0% | 41.45%
2024-03-28 06:00 | 3 | 28 | 6 | 0.3783% | 41.7%
2024-03-28 07:00 | 3 | 28 | 7 | 6.195% | 40.49%
2024-03-28 08:00 | 3 | 28 | 8 | 32.38% | 38.58%
2024-03-28 09:00 | 3 | 28 | 9 | 48.16% | 37.56%
2024-03-28 10:00 | 3 | 28 | 10 | 20.9% | 37.82%
2024-03-28 11:00 | 3 | 28 | 11 | 21.38% | 42.13%
2024-03-28 12:00 | 3 | 28 | 12 | 16.87% | 38.82%
2024-03-28 13:00 | 3 | 28 | 13 | 14.63% | 39.69%
2024-03-28 14:00 | 3 | 28 | 14 | 15.41% | 40.53%
2024-03-28 15:00 | 3 | 28 | 15 | 9.786% | 41.97%
2024-03-28 16:00 | 3 | 28 | 16 | 7.834% | 41.74%
2024-03-28 17:00 | 3 | 28 | 17 | 3.584% | 42.22%
2024-03-28 18:00 | 3 | 28 | 18 | 0% | 43.4%
2024-03-28 19:00 | 3 | 28 | 19 | 0% | 44.02%
2024-03-28 20:00 | 3 | 28 | 20 | 0% | 44.27%
2024-03-28 21:00 | 3 | 28 | 21 | 0% | 44.47%
2024-03-28 22:00 | 3 | 28 | 22 | 0% | 44.41%
2024-03-28 23:00 | 3 | 28 | 23 | 0% | 44.29%
2024-03-29 | 3 | 29 | 0 | 0% | 35.44%
2024-03-29 01:00 | 3 | 29 | 1 | 0% | 42.82%
2024-03-29 02:00 | 3 | 29 | 2 | 0% | 41.53%
2024-03-29 03:00 | 3 | 29 | 3 | 0% | 41.03%
2024-03-29 04:00 | 3 | 29 | 4 | 0% | 39.93%
2024-03-29 05:00 | 3 | 29 | 5 | 0% | 39.24%
2024-03-29 06:00 | 3 | 29 | 6 | 0.6363% | 38.01%
2024-03-29 07:00 | 3 | 29 | 7 | 4.305% | 36.34%
2024-03-29 08:00 | 3 | 29 | 8 | 9.503% | 35.13%
2024-03-29 09:00 | 3 | 29 | 9 | 19.98% | 34.79%
2024-03-29 10:00 | 3 | 29 | 10 | 20.55% | 35.19%
2024-03-29 11:00 | 3 | 29 | 11 | 25.69% | 35.45%
2024-03-29 12:00 | 3 | 29 | 12 | 28.11% | 36.07%
2024-03-29 13:00 | 3 | 29 | 13 | 27.1% | 36.45%
2024-03-29 14:00 | 3 | 29 | 14 | 14.42% | 36.82%
2024-03-29 15:00 | 3 | 29 | 15 | 11.04% | 37.3%
2024-03-29 16:00 | 3 | 29 | 16 | 21.9% | 36.51%
2024-03-29 17:00 | 3 | 29 | 17 | 8.385% | 35.18%
2024-03-29 18:00 | 3 | 29 | 18 | 0.2081% | 35.02%
2024-03-29 19:00 | 3 | 29 | 19 | 0% | 35.32%
2024-03-29 20:00 | 3 | 29 | 20 | 0% | 35.4%
2024-03-29 21:00 | 3 | 29 | 21 | 0% | 35.3%
2024-03-29 22:00 | 3 | 29 | 22 | 0% | 34.34%
2024-03-29 23:00 | 3 | 29 | 23 | 0% | 33.48%
2024-03-30 | 3 | 30 | 0 | 0% | 29.79%
2024-03-30 01:00 | 3 | 30 | 1 | 0% | 31.42%
2024-03-30 02:00 | 3 | 30 | 2 | 0% | 30.7%
2024-03-30 03:00 | 3 | 30 | 3 | 0% | 29.86%
2024-03-30 04:00 | 3 | 30 | 4 | 0% | 28.95%
2024-03-30 05:00 | 3 | 30 | 5 | 0% | 28.38%
2024-03-30 06:00 | 3 | 30 | 6 | 1.003% | 27.5%
2024-03-30 07:00 | 3 | 30 | 7 | 11.48% | 25.8%
2024-03-30 08:00 | 3 | 30 | 8 | 28.72% | 24.67%
2024-03-30 09:00 | 3 | 30 | 9 | 42.85% | 23.8%
2024-03-30 10:00 | 3 | 30 | 10 | 68.98% | 24.16%
2024-03-30 11:00 | 3 | 30 | 11 | 75.41% | 24.7%
2024-03-30 12:00 | 3 | 30 | 12 | 75.41% | 25.34%
2024-03-30 13:00 | 3 | 30 | 13 | 64.13% | 25.9%
2024-03-30 14:00 | 3 | 30 | 14 | 61.28% | 26.05%
2024-03-30 15:00 | 3 | 30 | 15 | 32.1% | 25.49%
2024-03-30 16:00 | 3 | 30 | 16 | 12.56% | 25.23%
2024-03-30 17:00 | 3 | 30 | 17 | 3.174% | 25.57%
2024-03-30 18:00 | 3 | 30 | 18 | 0% | 26.22%
2024-03-30 19:00 | 3 | 30 | 19 | 0% | 27.43%
2024-03-30 20:00 | 3 | 30 | 20 | 0% | 28.25%
2024-03-30 21:00 | 3 | 30 | 21 | 0% | 28.9%
2024-03-30 22:00 | 3 | 30 | 22 | 0% | 29.45%
2024-03-30 23:00 | 3 | 30 | 23 | 0% | 29.4%
2024-03-31 | 3 | 31 | 0 | 0% | 25.33%
2024-03-31 01:00 | 3 | 31 | 1 | 0% | 29.77%
2024-03-31 02:00 | 3 | 31 | 2 | 0% | 29.99%
2024-03-31 03:00 | 3 | 31 | 3 | 0% | 30.16%
2024-03-31 04:00 | 3 | 31 | 4 | 0% | 30.1%
2024-03-31 05:00 | 3 | 31 | 5 | 0% | 30.03%
2024-03-31 06:00 | 3 | 31 | 6 | 0.198% | 28.92%
2024-03-31 07:00 | 3 | 31 | 7 | 1.015% | 26.09%
2024-03-31 08:00 | 3 | 31 | 8 | 4.474% | 23.08%
2024-03-31 09:00 | 3 | 31 | 9 | 5.225% | 21.54%
2024-03-31 10:00 | 3 | 31 | 10 | 8.167% | 20.71%
2024-03-31 11:00 | 3 | 31 | 11 | 9.272% | 20.19%
2024-03-31 12:00 | 3 | 31 | 12 | 7.101% | 19.92%
2024-03-31 13:00 | 3 | 31 | 13 | 5.683% | 20.63%
2024-03-31 14:00 | 3 | 31 | 14 | 5.16% | 20.2%
2024-03-31 15:00 | 3 | 31 | 15 | 2.858% | 20.49%
2024-03-31 16:00 | 3 | 31 | 16 | 6.13% | 20.79%
2024-03-31 17:00 | 3 | 31 | 17 | 4.976% | 22.09%
2024-03-31 18:00 | 3 | 31 | 18 | 0% | 21.62%
2024-03-31 19:00 | 3 | 31 | 19 | 0% | 22.84%
2024-03-31 20:00 | 3 | 31 | 20 | 0% | 23.99%
2024-03-31 21:00 | 3 | 31 | 21 | 0% | 25.23%
2024-03-31 22:00 | 3 | 31 | 22 | 0% | 26.04%
2024-03-31 23:00 | 3 | 31 | 23 | 0% | 25.73%
2024-04-01 | 4 | 1 | 0 | 0% | 32.82%
2024-04-01 01:00 | 4 | 1 | 1 | 0% | 25.17%
2024-04-01 02:00 | 4 | 1 | 2 | 0% | 25.36%
2024-04-01 03:00 | 4 | 1 | 3 | 0% | 25.07%
2024-04-01 04:00 | 4 | 1 | 4 | 0% | 25.27%
2024-04-01 05:00 | 4 | 1 | 5 | 0% | 24.44%
2024-04-01 06:00 | 4 | 1 | 6 | 3.413% | 22.47%
2024-04-01 07:00 | 4 | 1 | 7 | 20.82% | 19.33%
2024-04-01 08:00 | 4 | 1 | 8 | 42% | 16.38%
2024-04-01 09:00 | 4 | 1 | 9 | 60.49% | 13.9%
2024-04-01 10:00 | 4 | 1 | 10 | 73.45% | 13.79%
2024-04-01 11:00 | 4 | 1 | 11 | 75.41% | 14.68%
2024-04-01 12:00 | 4 | 1 | 12 | 75.41% | 16.54%
2024-04-01 13:00 | 4 | 1 | 13 | 75.41% | 18.39%
2024-04-01 14:00 | 4 | 1 | 14 | 67.03% | 20.06%
2024-04-01 15:00 | 4 | 1 | 15 | 51.22% | 21.2%
2024-04-01 16:00 | 4 | 1 | 16 | 18.98% | 21.9%
2024-04-01 17:00 | 4 | 1 | 17 | 2.549% | 23.41%
2024-04-01 18:00 | 4 | 1 | 18 | 0.4843% | 24.59%
2024-04-01 19:00 | 4 | 1 | 19 | 0% | 26.8%
2024-04-01 20:00 | 4 | 1 | 20 | 0% | 29.17%
2024-04-01 21:00 | 4 | 1 | 21 | 0% | 32.9%
2024-04-01 22:00 | 4 | 1 | 22 | 0% | 31.84%
2024-04-01 23:00 | 4 | 1 | 23 | 0% | 32.38%
2024-04-02 | 4 | 2 | 0 | 0% | 35.24%
2024-04-02 01:00 | 4 | 2 | 1 | 0% | 32.85%
2024-04-02 02:00 | 4 | 2 | 2 | 0% | 33.01%
2024-04-02 03:00 | 4 | 2 | 3 | 0% | 33.55%
2024-04-02 04:00 | 4 | 2 | 4 | 0% | 34.04%
2024-04-02 05:00 | 4 | 2 | 5 | 0% | 33.94%
2024-04-02 06:00 | 4 | 2 | 6 | 0.7605% | 32.82%
2024-04-02 07:00 | 4 | 2 | 7 | 2.736% | 31.05%
2024-04-02 08:00 | 4 | 2 | 8 | 7.69% | 29.82%
2024-04-02 09:00 | 4 | 2 | 9 | 13.42% | 29.24%
2024-04-02 10:00 | 4 | 2 | 10 | 16.34% | 29.87%
2024-04-02 11:00 | 4 | 2 | 11 | 15.8% | 31.23%
2024-04-02 12:00 | 4 | 2 | 12 | 14.39% | 32.53%
2024-04-02 13:00 | 4 | 2 | 13 | 15.31% | 33.74%
2024-04-02 14:00 | 4 | 2 | 14 | 15.17% | 34.93%
2024-04-02 15:00 | 4 | 2 | 15 | 9.827% | 35.28%
2024-04-02 16:00 | 4 | 2 | 16 | 12.82% | 34.83%
2024-04-02 17:00 | 4 | 2 | 17 | 5.914% | 34.92%
2024-04-02 18:00 | 4 | 2 | 18 | 0.404% | 35.54%
2024-04-02 19:00 | 4 | 2 | 19 | 0% | 36.77%
2024-04-02 20:00 | 4 | 2 | 20 | 0% | 37.27%
2024-04-02 21:00 | 4 | 2 | 21 | 0% | 37.05%
2024-04-02 22:00 | 4 | 2 | 22 | 0% | 36.55%
2024-04-02 23:00 | 4 | 2 | 23 | 0% | 35.87%
2024-04-03 | 4 | 3 | 0 | 0% | 32.26%
2024-04-03 01:00 | 4 | 3 | 1 | 0% | 34.09%
2024-04-03 02:00 | 4 | 3 | 2 | 0% | 33.03%
2024-04-03 03:00 | 4 | 3 | 3 | 0% | 32.45%
2024-04-03 04:00 | 4 | 3 | 4 | 0% | 32.33%
2024-04-03 05:00 | 4 | 3 | 5 | 0% | 31.78%
2024-04-03 06:00 | 4 | 3 | 6 | 1.214% | 30.8%
2024-04-03 07:00 | 4 | 3 | 7 | 8.471% | 28.42%
2024-04-03 08:00 | 4 | 3 | 8 | 15.31% | 25.81%
2024-04-03 09:00 | 4 | 3 | 9 | 16.92% | 24.17%
2024-04-03 10:00 | 4 | 3 | 10 | 21.76% | 22.5%
2024-04-03 11:00 | 4 | 3 | 11 | 24.94% | 22.64%
2024-04-03 12:00 | 4 | 3 | 12 | 25.8% | 22.23%
2024-04-03 13:00 | 4 | 3 | 13 | 40.86% | 23.18%
2024-04-03 14:00 | 4 | 3 | 14 | 55.3% | 24.33%
2024-04-03 15:00 | 4 | 3 | 15 | 41.32% | 25.86%
2024-04-03 16:00 | 4 | 3 | 16 | 23.23% | 26.02%
2024-04-03 17:00 | 4 | 3 | 17 | 7.048% | 26.37%
2024-04-03 18:00 | 4 | 3 | 18 | 0.8222% | 28%
2024-04-03 19:00 | 4 | 3 | 19 | 0% | 30.74%
2024-04-03 20:00 | 4 | 3 | 20 | 0% | 30.96%
2024-04-03 21:00 | 4 | 3 | 21 | 0% | 31.98%
2024-04-03 22:00 | 4 | 3 | 22 | 0% | 32.38%
2024-04-03 23:00 | 4 | 3 | 23 | 0% | 32.1%
2024-04-04 | 4 | 4 | 0 | 0% | 38.35%
2024-04-04 01:00 | 4 | 4 | 1 | 0% | 32.92%
2024-04-04 02:00 | 4 | 4 | 2 | 0% | 33.4%
2024-04-04 03:00 | 4 | 4 | 3 | 0% | 34.85%
2024-04-04 04:00 | 4 | 4 | 4 | 0% | 36.14%
2024-04-04 05:00 | 4 | 4 | 5 | 0% | 36.97%
2024-04-04 06:00 | 4 | 4 | 6 | 1.766% | 36.32%
2024-04-04 07:00 | 4 | 4 | 7 | 3.419% | 34.29%
2024-04-04 08:00 | 4 | 4 | 8 | 9.439% | 32.53%
2024-04-04 09:00 | 4 | 4 | 9 | 10.5% | 32.43%
2024-04-04 10:00 | 4 | 4 | 10 | 19.55% | 32.89%
2024-04-04 11:00 | 4 | 4 | 11 | 9.86% | 33.46%
2024-04-04 12:00 | 4 | 4 | 12 | 19.82% | 34.19%
2024-04-04 13:00 | 4 | 4 | 13 | 14.31% | 35.05%
2024-04-04 14:00 | 4 | 4 | 14 | 7.34% | 35.84%
2024-04-04 15:00 | 4 | 4 | 15 | 7.824% | 36.65%
2024-04-04 16:00 | 4 | 4 | 16 | 6.839% | 36.94%
2024-04-04 17:00 | 4 | 4 | 17 | 3.946% | 36.98%
2024-04-04 18:00 | 4 | 4 | 18 | 0.4032% | 37.81%
2024-04-04 19:00 | 4 | 4 | 19 | 0% | 39.53%
2024-04-04 20:00 | 4 | 4 | 20 | 0% | 40.41%
2024-04-04 21:00 | 4 | 4 | 21 | 0% | 40.6%
2024-04-04 22:00 | 4 | 4 | 22 | 0% | 40.19%
2024-04-04 23:00 | 4 | 4 | 23 | 0% | 39.51%
2024-04-05 | 4 | 5 | 0 | 0% | 32.34%
2024-04-05 01:00 | 4 | 5 | 1 | 0% | 40.04%
2024-04-05 02:00 | 4 | 5 | 2 | 0% | 37.43%
2024-04-05 03:00 | 4 | 5 | 3 | 0% | 37.28%
2024-04-05 04:00 | 4 | 5 | 4 | 0% | 36.86%
2024-04-05 05:00 | 4 | 5 | 5 | 0% | 35.93%
2024-04-05 06:00 | 4 | 5 | 6 | 3.596% | 34.19%
2024-04-05 07:00 | 4 | 5 | 7 | 14.71% | 31.39%
2024-04-05 08:00 | 4 | 5 | 8 | 27.32% | 29.06%
2024-04-05 09:00 | 4 | 5 | 9 | 38.68% | 28.16%
2024-04-05 10:00 | 4 | 5 | 10 | 48.57% | 28.06%
2024-04-05 11:00 | 4 | 5 | 11 | 62.01% | 28.61%
2024-04-05 12:00 | 4 | 5 | 12 | 75.41% | 28.89%
2024-04-05 13:00 | 4 | 5 | 13 | 40% | 29.41%
2024-04-05 14:00 | 4 | 5 | 14 | 55.01% | 31.54%
2024-04-05 15:00 | 4 | 5 | 15 | 54.56% | 29.05%
2024-04-05 16:00 | 4 | 5 | 16 | 33.1% | 28.48%
2024-04-05 17:00 | 4 | 5 | 17 | 11.42% | 27.12%
2024-04-05 18:00 | 4 | 5 | 18 | 1.033% | 27.69%
2024-04-05 19:00 | 4 | 5 | 19 | 0% | 29.2%
2024-04-05 20:00 | 4 | 5 | 20 | 0% | 31.05%
2024-04-05 21:00 | 4 | 5 | 21 | 0% | 32.76%
2024-04-05 22:00 | 4 | 5 | 22 | 0% | 35.93%
2024-04-05 23:00 | 4 | 5 | 23 | 0% | 32.83%
2024-04-06 | 4 | 6 | 0 | 0% | 34.21%
2024-04-06 01:00 | 4 | 6 | 1 | 0% | 32.14%
2024-04-06 02:00 | 4 | 6 | 2 | 0% | 32%
2024-04-06 03:00 | 4 | 6 | 3 | 0% | 31.92%
2024-04-06 04:00 | 4 | 6 | 4 | 0% | 31.69%
2024-04-06 05:00 | 4 | 6 | 5 | 0% | 31.04%
2024-04-06 06:00 | 4 | 6 | 6 | 2.235% | 29.85%
2024-04-06 07:00 | 4 | 6 | 7 | 8.081% | 27.28%
2024-04-06 08:00 | 4 | 6 | 8 | 19.88% | 24.99%
2024-04-06 09:00 | 4 | 6 | 9 | 18.95% | 23.87%
2024-04-06 10:00 | 4 | 6 | 10 | 21.49% | 24.37%
2024-04-06 11:00 | 4 | 6 | 11 | 21.51% | 25.54%
2024-04-06 12:00 | 4 | 6 | 12 | 14.5% | 26.54%
2024-04-06 13:00 | 4 | 6 | 13 | 15.19% | 27.75%
2024-04-06 14:00 | 4 | 6 | 14 | 16.14% | 29.01%
2024-04-06 15:00 | 4 | 6 | 15 | 22.67% | 29.71%
2024-04-06 16:00 | 4 | 6 | 16 | 12.45% | 28.77%
2024-04-06 17:00 | 4 | 6 | 17 | 9.026% | 28.17%
2024-04-06 18:00 | 4 | 6 | 18 | 1.277% | 28.91%
2024-04-06 19:00 | 4 | 6 | 19 | 0% | 31.21%
2024-04-06 20:00 | 4 | 6 | 20 | 0% | 33.08%
2024-04-06 21:00 | 4 | 6 | 21 | 0% | 34.06%
2024-04-06 22:00 | 4 | 6 | 22 | 0% | 34.56%
2024-04-06 23:00 | 4 | 6 | 23 | 0% | 34.22%
2024-04-07 | 4 | 7 | 0 | 0% | 31.3%
2024-04-07 01:00 | 4 | 7 | 1 | 0% | 34.27%
2024-04-07 02:00 | 4 | 7 | 2 | 0% | 34.74%
2024-04-07 03:00 | 4 | 7 | 3 | 0% | 34.77%
2024-04-07 04:00 | 4 | 7 | 4 | 0% | 34.75%
2024-04-07 05:00 | 4 | 7 | 5 | 0% | 34.44%
2024-04-07 06:00 | 4 | 7 | 6 | 4.398% | 33.44%
2024-04-07 07:00 | 4 | 7 | 7 | 24.72% | 31.18%
2024-04-07 08:00 | 4 | 7 | 8 | 46.78% | 30.32%
2024-04-07 09:00 | 4 | 7 | 9 | 64.82% | 30.39%
2024-04-07 10:00 | 4 | 7 | 10 | 75.41% | 31.27%
2024-04-07 11:00 | 4 | 7 | 11 | 71.11% | 32.34%
2024-04-07 12:00 | 4 | 7 | 12 | 63.75% | 35.56%
2024-04-07 13:00 | 4 | 7 | 13 | 73.95% | 33.07%
2024-04-07 14:00 | 4 | 7 | 14 | 70.56% | 32.97%
2024-04-07 15:00 | 4 | 7 | 15 | 55.01% | 32.09%
2024-04-07 16:00 | 4 | 7 | 16 | 33.63% | 30.83%
2024-04-07 17:00 | 4 | 7 | 17 | 10.64% | 29.29%
2024-04-07 18:00 | 4 | 7 | 18 | 1.529% | 29.43%
2024-04-07 19:00 | 4 | 7 | 19 | 0% | 30.39%
2024-04-07 20:00 | 4 | 7 | 20 | 0% | 34.02%
2024-04-07 21:00 | 4 | 7 | 21 | 0% | 31.83%
2024-04-07 22:00 | 4 | 7 | 22 | 0% | 32.46%
2024-04-07 23:00 | 4 | 7 | 23 | 0% | 31.9%
2024-04-08 | 4 | 8 | 0 | 0% | 35.44%
2024-04-08 01:00 | 4 | 8 | 1 | 0% | 30.91%
2024-04-08 02:00 | 4 | 8 | 2 | 0% | 30.78%
2024-04-08 03:00 | 4 | 8 | 3 | 0% | 31.55%
2024-04-08 04:00 | 4 | 8 | 4 | 0% | 31.68%
2024-04-08 05:00 | 4 | 8 | 5 | 0% | 31.53%
2024-04-08 06:00 | 4 | 8 | 6 | 4.665% | 30.68%
2024-04-08 07:00 | 4 | 8 | 7 | 14.23% | 28.4%
2024-04-08 08:00 | 4 | 8 | 8 | 33.84% | 27.16%
2024-04-08 09:00 | 4 | 8 | 9 | 63% | 26.96%
2024-04-08 10:00 | 4 | 8 | 10 | 75.41% | 27.93%
2024-04-08 11:00 | 4 | 8 | 11 | 75.41% | 28.95%
2024-04-08 12:00 | 4 | 8 | 12 | 75.41% | 30.45%
2024-04-08 13:00 | 4 | 8 | 13 | 75.41% | 31.31%
2024-04-08 14:00 | 4 | 8 | 14 | 68.88% | 32.31%
2024-04-08 15:00 | 4 | 8 | 15 | 53.53% | 32.3%
2024-04-08 16:00 | 4 | 8 | 16 | 32.78% | 31.5%
2024-04-08 17:00 | 4 | 8 | 17 | 11.9% | 30.35%
2024-04-08 18:00 | 4 | 8 | 18 | 1.364% | 30.33%
2024-04-08 19:00 | 4 | 8 | 19 | 0% | 31.97%
2024-04-08 20:00 | 4 | 8 | 20 | 0% | 33.68%
2024-04-08 21:00 | 4 | 8 | 21 | 0% | 36.28%
2024-04-08 22:00 | 4 | 8 | 22 | 0% | 35.87%
2024-04-08 23:00 | 4 | 8 | 23 | 0% | 35.56%
2024-04-09 | 4 | 9 | 0 | 0% | 36.63%
2024-04-09 01:00 | 4 | 9 | 1 | 0% | 36.06%
2024-04-09 02:00 | 4 | 9 | 2 | 0% | 37.16%
2024-04-09 03:00 | 4 | 9 | 3 | 0% | 37.65%
2024-04-09 04:00 | 4 | 9 | 4 | 0% | 38.19%
2024-04-09 05:00 | 4 | 9 | 5 | 0% | 38.1%
2024-04-09 06:00 | 4 | 9 | 6 | 2.145% | 37.33%
2024-04-09 07:00 | 4 | 9 | 7 | 12.88% | 35.06%
2024-04-09 08:00 | 4 | 9 | 8 | 29.76% | 33.81%
2024-04-09 09:00 | 4 | 9 | 9 | 64.77% | 33.82%
2024-04-09 10:00 | 4 | 9 | 10 | 61.79% | 34.64%
2024-04-09 11:00 | 4 | 9 | 11 | 56.96% | 34.69%
2024-04-09 12:00 | 4 | 9 | 12 | 75.41% | 35.34%
2024-04-09 13:00 | 4 | 9 | 13 | 75.41% | 38.98%
2024-04-09 14:00 | 4 | 9 | 14 | 53.7% | 37.15%
2024-04-09 15:00 | 4 | 9 | 15 | 41.74% | 37.35%
2024-04-09 16:00 | 4 | 9 | 16 | 33.32% | 36.83%
2024-04-09 17:00 | 4 | 9 | 17 | 10.54% | 35.85%
2024-04-09 18:00 | 4 | 9 | 18 | 1.735% | 36.03%
2024-04-09 19:00 | 4 | 9 | 19 | 0% | 37.3%
2024-04-09 20:00 | 4 | 9 | 20 | 0% | 38.47%
2024-04-09 21:00 | 4 | 9 | 21 | 0% | 39.47%
2024-04-09 22:00 | 4 | 9 | 22 | 0% | 38.65%
2024-04-09 23:00 | 4 | 9 | 23 | 0% | 37.44%
2024-04-10 | 4 | 10 | 0 | 0% | 40.3%
2024-04-10 01:00 | 4 | 10 | 1 | 0% | 36.68%
2024-04-10 02:00 | 4 | 10 | 2 | 0% | 36.12%
2024-04-10 03:00 | 4 | 10 | 3 | 0% | 36.1%
2024-04-10 04:00 | 4 | 10 | 4 | 0% | 36.04%
2024-04-10 05:00 | 4 | 10 | 5 | 0.2277% | 36.03%
2024-04-10 06:00 | 4 | 10 | 6 | 4.81% | 35.63%
2024-04-10 07:00 | 4 | 10 | 7 | 22.21% | 33.78%
2024-04-10 08:00 | 4 | 10 | 8 | 28.78% | 35.01%
2024-04-10 09:00 | 4 | 10 | 9 | 46.62% | 35.65%
2024-04-10 10:00 | 4 | 10 | 10 | 63.47% | 37.94%
2024-04-10 11:00 | 4 | 10 | 11 | 75.41% | 40.4%
2024-04-10 12:00 | 4 | 10 | 12 | 75.41% | 42.35%
2024-04-10 13:00 | 4 | 10 | 13 | 74.39% | 44.42%
2024-04-10 14:00 | 4 | 10 | 14 | 63.96% | 45.36%
2024-04-10 15:00 | 4 | 10 | 15 | 48.52% | 45.16%
2024-04-10 16:00 | 4 | 10 | 16 | 29.36% | 43.89%
2024-04-10 17:00 | 4 | 10 | 17 | 11.03% | 43.4%
2024-04-10 18:00 | 4 | 10 | 18 | 1.785% | 43.53%
2024-04-10 19:00 | 4 | 10 | 19 | 0% | 44.55%
2024-04-10 20:00 | 4 | 10 | 20 | 0% | 45.01%
2024-04-10 21:00 | 4 | 10 | 21 | 0% | 44.45%
2024-04-10 22:00 | 4 | 10 | 22 | 0% | 42.49%
2024-04-10 23:00 | 4 | 10 | 23 | 0% | 40.26%
2024-04-11 | 4 | 11 | 0 | 0% | 34.96%
2024-04-11 01:00 | 4 | 11 | 1 | 0% | 35.75%
2024-04-11 02:00 | 4 | 11 | 2 | 0% | 34.15%
2024-04-11 03:00 | 4 | 11 | 3 | 0% | 32.45%
2024-04-11 04:00 | 4 | 11 | 4 | 0% | 31.63%
2024-04-11 05:00 | 4 | 11 | 5 | 0.4101% | 30.17%
2024-04-11 06:00 | 4 | 11 | 6 | 6.265% | 28.26%
2024-04-11 07:00 | 4 | 11 | 7 | 23.72% | 25.66%
2024-04-11 08:00 | 4 | 11 | 8 | 44.22% | 23.85%
2024-04-11 09:00 | 4 | 11 | 9 | 61.41% | 23.31%
2024-04-11 10:00 | 4 | 11 | 10 | 67.84% | 23.62%
2024-04-11 11:00 | 4 | 11 | 11 | 46.78% | 24.46%
2024-04-11 12:00 | 4 | 11 | 12 | 35.22% | 28.34%
2024-04-11 13:00 | 4 | 11 | 13 | 42.38% | 27.51%
2024-04-11 14:00 | 4 | 11 | 14 | 21.46% | 28.59%
2024-04-11 15:00 | 4 | 11 | 15 | 11.57% | 29.21%
2024-04-11 16:00 | 4 | 11 | 16 | 9.725% | 29.3%
2024-04-11 17:00 | 4 | 11 | 17 | 5.649% | 28.93%
2024-04-11 18:00 | 4 | 11 | 18 | 1.347% | 29.93%
2024-04-11 19:00 | 4 | 11 | 19 | 0% | 32.17%
2024-04-11 20:00 | 4 | 11 | 20 | 0% | 33.73%
2024-04-11 21:00 | 4 | 11 | 21 | 0% | 34.87%
2024-04-11 22:00 | 4 | 11 | 22 | 0% | 38.53%
2024-04-11 23:00 | 4 | 11 | 23 | 0% | 35.54%
2024-04-12 | 4 | 12 | 0 | 0% | 31.68%
2024-04-12 01:00 | 4 | 12 | 1 | 0% | 34.12%
2024-04-12 02:00 | 4 | 12 | 2 | 0% | 33.68%
2024-04-12 03:00 | 4 | 12 | 3 | 0% | 33.63%
2024-04-12 04:00 | 4 | 12 | 4 | 0% | 33.07%
2024-04-12 05:00 | 4 | 12 | 5 | 0% | 32.22%
2024-04-12 06:00 | 4 | 12 | 6 | 1.053% | 30.55%
2024-04-12 07:00 | 4 | 12 | 7 | 2.488% | 28.13%
2024-04-12 08:00 | 4 | 12 | 8 | 9.502% | 26.87%
2024-04-12 09:00 | 4 | 12 | 9 | 16.17% | 24.26%
2024-04-12 10:00 | 4 | 12 | 10 | 15.1% | 25.58%
2024-04-12 11:00 | 4 | 12 | 11 | 16.51% | 26.51%
2024-04-12 12:00 | 4 | 12 | 12 | 26.5% | 27.26%
2024-04-12 13:00 | 4 | 12 | 13 | 30.52% | 27.91%
2024-04-12 14:00 | 4 | 12 | 14 | 19.37% | 28.15%
2024-04-12 15:00 | 4 | 12 | 15 | 13.87% | 28.37%
2024-04-12 16:00 | 4 | 12 | 16 | 8.933% | 27.93%
2024-04-12 17:00 | 4 | 12 | 17 | 9.626% | 27.61%
2024-04-12 18:00 | 4 | 12 | 18 | 2.114% | 28.29%
2024-04-12 19:00 | 4 | 12 | 19 | 0% | 30.08%
2024-04-12 20:00 | 4 | 12 | 20 | 0% | 31.46%
2024-04-12 21:00 | 4 | 12 | 21 | 0% | 32.27%
2024-04-12 22:00 | 4 | 12 | 22 | 0% | 32.47%
2024-04-12 23:00 | 4 | 12 | 23 | 0% | 32.25%
2024-04-13 | 4 | 13 | 0 | 0% | 34.23%
2024-04-13 01:00 | 4 | 13 | 1 | 0% | 32.33%
2024-04-13 02:00 | 4 | 13 | 2 | 0% | 32.48%
2024-04-13 03:00 | 4 | 13 | 3 | 0% | 32.81%
2024-04-13 04:00 | 4 | 13 | 4 | 0% | 33.66%
2024-04-13 05:00 | 4 | 13 | 5 | 0.8368% | 34.15%
2024-04-13 06:00 | 4 | 13 | 6 | 7.536% | 34.09%
2024-04-13 07:00 | 4 | 13 | 7 | 28.04% | 33.9%
2024-04-13 08:00 | 4 | 13 | 8 | 49.71% | 33.46%
2024-04-13 09:00 | 4 | 13 | 9 | 66.54% | 33.84%
2024-04-13 10:00 | 4 | 13 | 10 | 71.37% | 34.43%
2024-04-13 11:00 | 4 | 13 | 11 | 63.84% | 35.29%
2024-04-13 12:00 | 4 | 13 | 12 | 27.93% | 36.37%
2024-04-13 13:00 | 4 | 13 | 13 | 35.73% | 36.91%
2024-04-13 14:00 | 4 | 13 | 14 | 64.56% | 37.11%
2024-04-13 15:00 | 4 | 13 | 15 | 55.55% | 38.49%
2024-04-13 16:00 | 4 | 13 | 16 | 35.05% | 39.73%
2024-04-13 17:00 | 4 | 13 | 17 | 13.57% | 38.82%
2024-04-13 18:00 | 4 | 13 | 18 | 2.354% | 38.95%
2024-04-13 19:00 | 4 | 13 | 19 | 0% | 38.31%
2024-04-13 20:00 | 4 | 13 | 20 | 0% | 38.42%
2024-04-13 21:00 | 4 | 13 | 21 | 0% | 37.62%
2024-04-13 22:00 | 4 | 13 | 22 | 0% | 36.19%
2024-04-13 23:00 | 4 | 13 | 23 | 0% | 35.3%
2024-04-14 | 4 | 14 | 0 | 0% | 30.25%
2024-04-14 01:00 | 4 | 14 | 1 | 0% | 34.49%
2024-04-14 02:00 | 4 | 14 | 2 | 0% | 34.7%
2024-04-14 03:00 | 4 | 14 | 3 | 0% | 35.1%
2024-04-14 04:00 | 4 | 14 | 4 | 0% | 35.35%
2024-04-14 05:00 | 4 | 14 | 5 | 0.9032% | 34.82%
2024-04-14 06:00 | 4 | 14 | 6 | 3.791% | 32.97%
2024-04-14 07:00 | 4 | 14 | 7 | 9.434% | 31.09%
2024-04-14 08:00 | 4 | 14 | 8 | 16.48% | 30.38%
2024-04-14 09:00 | 4 | 14 | 9 | 22.94% | 30.09%
2024-04-14 10:00 | 4 | 14 | 10 | 22.41% | 30.44%
2024-04-14 11:00 | 4 | 14 | 11 | 21.84% | 31.32%
2024-04-14 12:00 | 4 | 14 | 12 | 27.44% | 31.99%
2024-04-14 13:00 | 4 | 14 | 13 | 64.99% | 32.25%
2024-04-14 14:00 | 4 | 14 | 14 | 71.83% | 32.32%
2024-04-14 15:00 | 4 | 14 | 15 | 56.9% | 31.55%
2024-04-14 16:00 | 4 | 14 | 16 | 35.66% | 30.56%
2024-04-14 17:00 | 4 | 14 | 17 | 13.04% | 30.34%
2024-04-14 18:00 | 4 | 14 | 18 | 2.746% | 30.69%
2024-04-14 19:00 | 4 | 14 | 19 | 0% | 31.26%
2024-04-14 20:00 | 4 | 14 | 20 | 0% | 31.79%
2024-04-14 21:00 | 4 | 14 | 21 | 0% | 31.87%
2024-04-14 22:00 | 4 | 14 | 22 | 0% | 32.11%
2024-04-14 23:00 | 4 | 14 | 23 | 0% | 30.82%
2024-04-15 | 4 | 15 | 0 | 0% | 29.48%
2024-04-15 01:00 | 4 | 15 | 1 | 0% | 29.29%
2024-04-15 02:00 | 4 | 15 | 2 | 0% | 28.63%
2024-04-15 03:00 | 4 | 15 | 3 | 0% | 27.74%
2024-04-15 04:00 | 4 | 15 | 4 | 0% | 27.15%
2024-04-15 05:00 | 4 | 15 | 5 | 0.8279% | 26.17%
2024-04-15 06:00 | 4 | 15 | 6 | 6.307% | 23.87%
2024-04-15 07:00 | 4 | 15 | 7 | 26.01% | 20.68%
2024-04-15 08:00 | 4 | 15 | 8 | 38.98% | 18.77%
2024-04-15 09:00 | 4 | 15 | 9 | 56.06% | 18.41%
2024-04-15 10:00 | 4 | 15 | 10 | 45.97% | 18.81%
2024-04-15 11:00 | 4 | 15 | 11 | 74.84% | 19.06%
2024-04-15 12:00 | 4 | 15 | 12 | 75.41% | 20.54%
2024-04-15 13:00 | 4 | 15 | 13 | 75.41% | 20.06%
2024-04-15 14:00 | 4 | 15 | 14 | 73.32% | 20.31%
2024-04-15 15:00 | 4 | 15 | 15 | 57.4% | 20.86%
2024-04-15 16:00 | 4 | 15 | 16 | 36.31% | 21.56%
2024-04-15 17:00 | 4 | 15 | 17 | 12.4% | 22.46%
2024-04-15 18:00 | 4 | 15 | 18 | 2.916% | 24.33%
2024-04-15 19:00 | 4 | 15 | 19 | 0% | 26.77%
2024-04-15 20:00 | 4 | 15 | 20 | 0% | 28.48%
2024-04-15 21:00 | 4 | 15 | 21 | 0% | 28.93%
2024-04-15 22:00 | 4 | 15 | 22 | 0% | 29.04%
2024-04-15 23:00 | 4 | 15 | 23 | 0% | 29.81%
2024-04-16 | 4 | 16 | 0 | 0% | 19.68%
2024-04-16 01:00 | 4 | 16 | 1 | 0% | 30.9%
2024-04-16 02:00 | 4 | 16 | 2 | 0% | 29.78%
2024-04-16 03:00 | 4 | 16 | 3 | 0% | 29.66%
2024-04-16 04:00 | 4 | 16 | 4 | 0% | 29.51%
2024-04-16 05:00 | 4 | 16 | 5 | 0.945% | 28.07%
2024-04-16 06:00 | 4 | 16 | 6 | 6.038% | 25.11%
2024-04-16 07:00 | 4 | 16 | 7 | 25.56% | 21.44%
2024-04-16 08:00 | 4 | 16 | 8 | 51.34% | 19.16%
2024-04-16 09:00 | 4 | 16 | 9 | 68.04% | 18.18%
2024-04-16 10:00 | 4 | 16 | 10 | 75.41% | 17.94%
2024-04-16 11:00 | 4 | 16 | 11 | 75.41% | 19.44%
2024-04-16 12:00 | 4 | 16 | 12 | 57.88% | 17.7%
2024-04-16 13:00 | 4 | 16 | 13 | 33.38% | 18.71%
2024-04-16 14:00 | 4 | 16 | 14 | 10.63% | 18.39%
2024-04-16 15:00 | 4 | 16 | 15 | 17.6% | 18.07%
2024-04-16 16:00 | 4 | 16 | 16 | 10.68% | 18.85%
2024-04-16 17:00 | 4 | 16 | 17 | 4.856% | 16.14%
2024-04-16 18:00 | 4 | 16 | 18 | 1.542% | 16.35%
2024-04-16 19:00 | 4 | 16 | 19 | 0% | 17.71%
2024-04-16 20:00 | 4 | 16 | 20 | 0% | 19.48%
2024-04-16 21:00 | 4 | 16 | 21 | 0% | 20.21%
2024-04-16 22:00 | 4 | 16 | 22 | 0% | 20.52%
2024-04-16 23:00 | 4 | 16 | 23 | 0% | 20.16%
2024-04-17 | 4 | 17 | 0 | 0% | 22.16%
2024-04-17 01:00 | 4 | 17 | 1 | 0% | 19.17%
2024-04-17 02:00 | 4 | 17 | 2 | 0% | 18.65%
2024-04-17 03:00 | 4 | 17 | 3 | 0% | 19.06%
2024-04-17 04:00 | 4 | 17 | 4 | 0% | 19.28%
2024-04-17 05:00 | 4 | 17 | 5 | 0.2289% | 19.02%
2024-04-17 06:00 | 4 | 17 | 6 | 5.37% | 17.92%
2024-04-17 07:00 | 4 | 17 | 7 | 18.41% | 16.09%
2024-04-17 08:00 | 4 | 17 | 8 | 42.47% | 14.75%
2024-04-17 09:00 | 4 | 17 | 9 | 63.42% | 14.68%
2024-04-17 10:00 | 4 | 17 | 10 | 75.41% | 15.31%
2024-04-17 11:00 | 4 | 17 | 11 | 75.41% | 14.32%
2024-04-17 12:00 | 4 | 17 | 12 | 75.41% | 16.22%
2024-04-17 13:00 | 4 | 17 | 13 | 71.29% | 16.71%
2024-04-17 14:00 | 4 | 17 | 14 | 69.45% | 17.2%
2024-04-17 15:00 | 4 | 17 | 15 | 54.64% | 17.18%
2024-04-17 16:00 | 4 | 17 | 16 | 34.6% | 17.35%
2024-04-17 17:00 | 4 | 17 | 17 | 13.04% | 17.57%
2024-04-17 18:00 | 4 | 17 | 18 | 3.057% | 18.46%
2024-04-17 19:00 | 4 | 17 | 19 | 0% | 19.92%
2024-04-17 20:00 | 4 | 17 | 20 | 0% | 21.26%
2024-04-17 21:00 | 4 | 17 | 21 | 0% | 21%
2024-04-17 22:00 | 4 | 17 | 22 | 0% | 22.23%
2024-04-17 23:00 | 4 | 17 | 23 | 0% | 22.33%
2024-04-18 | 4 | 18 | 0 | 0% | 21.09%
2024-04-18 01:00 | 4 | 18 | 1 | 0% | 22.37%
2024-04-18 02:00 | 4 | 18 | 2 | 0% | 22.41%
2024-04-18 03:00 | 4 | 18 | 3 | 0% | 22.3%
2024-04-18 04:00 | 4 | 18 | 4 | 0% | 21.9%
2024-04-18 05:00 | 4 | 18 | 5 | 1.59% | 20.74%
2024-04-18 06:00 | 4 | 18 | 6 | 10.71% | 19.02%
2024-04-18 07:00 | 4 | 18 | 7 | 31.42% | 16.86%
2024-04-18 08:00 | 4 | 18 | 8 | 53.24% | 15.37%
2024-04-18 09:00 | 4 | 18 | 9 | 70.16% | 15.25%
2024-04-18 10:00 | 4 | 18 | 10 | 75.41% | 15.73%
2024-04-18 11:00 | 4 | 18 | 11 | 75.41% | 16.42%
2024-04-18 12:00 | 4 | 18 | 12 | 75.41% | 16.81%
2024-04-18 13:00 | 4 | 18 | 13 | 75.41% | 15.79%
2024-04-18 14:00 | 4 | 18 | 14 | 62% | 17.11%
2024-04-18 15:00 | 4 | 18 | 15 | 46.29% | 17.21%
2024-04-18 16:00 | 4 | 18 | 16 | 36.54% | 16.86%
2024-04-18 17:00 | 4 | 18 | 17 | 13.2% | 17.11%
2024-04-18 18:00 | 4 | 18 | 18 | 2.969% | 17.55%
2024-04-18 19:00 | 4 | 18 | 19 | 0% | 18.71%
2024-04-18 20:00 | 4 | 18 | 20 | 0% | 20.06%
2024-04-18 21:00 | 4 | 18 | 21 | 0% | 21.03%
2024-04-18 22:00 | 4 | 18 | 22 | 0% | 21.47%
2024-04-18 23:00 | 4 | 18 | 23 | 0% | 20.95%
2024-04-19 | 4 | 19 | 0 | 0% | 28.15%
2024-04-19 01:00 | 4 | 19 | 1 | 0% | 20.88%
2024-04-19 02:00 | 4 | 19 | 2 | 0% | 20.68%
2024-04-19 03:00 | 4 | 19 | 3 | 0% | 20.69%
2024-04-19 04:00 | 4 | 19 | 4 | 0% | 20.38%
2024-04-19 05:00 | 4 | 19 | 5 | 1.711% | 19.85%
2024-04-19 06:00 | 4 | 19 | 6 | 11.09% | 18.54%
2024-04-19 07:00 | 4 | 19 | 7 | 32.26% | 16.85%
2024-04-19 08:00 | 4 | 19 | 8 | 53.59% | 16.38%
2024-04-19 09:00 | 4 | 19 | 9 | 69.83% | 16.84%
2024-04-19 10:00 | 4 | 19 | 10 | 75.41% | 19.72%
2024-04-19 11:00 | 4 | 19 | 11 | 75.41% | 19.27%
2024-04-19 12:00 | 4 | 19 | 12 | 75.41% | 20.46%
2024-04-19 13:00 | 4 | 19 | 13 | 75.41% | 21.21%
2024-04-19 14:00 | 4 | 19 | 14 | 73.32% | 22.09%
2024-04-19 15:00 | 4 | 19 | 15 | 58.47% | 22.23%
2024-04-19 16:00 | 4 | 19 | 16 | 37.62% | 22.17%
2024-04-19 17:00 | 4 | 19 | 17 | 15.61% | 22.2%
2024-04-19 18:00 | 4 | 19 | 18 | 2.627% | 22.78%
2024-04-19 19:00 | 4 | 19 | 19 | 0% | 24.03%
2024-04-19 20:00 | 4 | 19 | 20 | 0% | 25.68%
2024-04-19 21:00 | 4 | 19 | 21 | 0% | 27.35%
2024-04-19 22:00 | 4 | 19 | 22 | 0% | 28.53%
2024-04-19 23:00 | 4 | 19 | 23 | 0% | 28.1%
2024-04-20 | 4 | 20 | 0 | 0% | 27.56%
2024-04-20 01:00 | 4 | 20 | 1 | 0% | 27.67%
2024-04-20 02:00 | 4 | 20 | 2 | 0% | 27.72%
2024-04-20 03:00 | 4 | 20 | 3 | 0% | 27.93%
2024-04-20 04:00 | 4 | 20 | 4 | 0% | 27.79%
2024-04-20 05:00 | 4 | 20 | 5 | 1.866% | 27.12%
2024-04-20 06:00 | 4 | 20 | 6 | 11.1% | 24.9%
2024-04-20 07:00 | 4 | 20 | 7 | 28.63% | 22.18%
2024-04-20 08:00 | 4 | 20 | 8 | 20.66% | 20.59%
2024-04-20 09:00 | 4 | 20 | 9 | 41% | 20.15%
2024-04-20 10:00 | 4 | 20 | 10 | 74.6% | 20.22%
2024-04-20 11:00 | 4 | 20 | 11 | 75.41% | 20.6%
2024-04-20 12:00 | 4 | 20 | 12 | 75.41% | 21.32%
2024-04-20 13:00 | 4 | 20 | 13 | 75.41% | 21.62%
2024-04-20 14:00 | 4 | 20 | 14 | 73.47% | 22.45%
2024-04-20 15:00 | 4 | 20 | 15 | 58.75% | 22.74%
2024-04-20 16:00 | 4 | 20 | 16 | 38% | 22.74%
2024-04-20 17:00 | 4 | 20 | 17 | 15.93% | 22.87%
2024-04-20 18:00 | 4 | 20 | 18 | 2.723% | 23.21%
2024-04-20 19:00 | 4 | 20 | 19 | 0% | 24.35%
2024-04-20 20:00 | 4 | 20 | 20 | 0% | 25.77%
2024-04-20 21:00 | 4 | 20 | 21 | 0% | 26.36%
2024-04-20 22:00 | 4 | 20 | 22 | 0% | 26.96%
2024-04-20 23:00 | 4 | 20 | 23 | 0% | 27.39%
2024-04-21 | 4 | 21 | 0 | 0% | 29.05%
2024-04-21 01:00 | 4 | 21 | 1 | 0% | 28.32%
2024-04-21 02:00 | 4 | 21 | 2 | 0% | 28.55%
2024-04-21 03:00 | 4 | 21 | 3 | 0% | 28.84%
2024-04-21 04:00 | 4 | 21 | 4 | 0% | 29.01%
2024-04-21 05:00 | 4 | 21 | 5 | 2.123% | 28.06%
2024-04-21 06:00 | 4 | 21 | 6 | 10.78% | 25.73%
2024-04-21 07:00 | 4 | 21 | 7 | 32.78% | 23.04%
2024-04-21 08:00 | 4 | 21 | 8 | 54.06% | 21.76%
2024-04-21 09:00 | 4 | 21 | 9 | 70% | 21.67%
2024-04-21 10:00 | 4 | 21 | 10 | 75.41% | 22.74%
2024-04-21 11:00 | 4 | 21 | 11 | 75.41% | 24.31%
2024-04-21 12:00 | 4 | 21 | 12 | 75.41% | 27.59%
2024-04-21 13:00 | 4 | 21 | 13 | 75.41% | 26.28%
2024-04-21 14:00 | 4 | 21 | 14 | 73.76% | 26.56%
2024-04-21 15:00 | 4 | 21 | 15 | 58.9% | 26.34%
2024-04-21 16:00 | 4 | 21 | 16 | 38.26% | 26%
2024-04-21 17:00 | 4 | 21 | 17 | 16.29% | 25.37%
2024-04-21 18:00 | 4 | 21 | 18 | 2.827% | 24.71%
2024-04-21 19:00 | 4 | 21 | 19 | 0% | 24.82%
2024-04-21 20:00 | 4 | 21 | 20 | 0% | 26.57%
2024-04-21 21:00 | 4 | 21 | 21 | 0% | 27.54%
2024-04-21 22:00 | 4 | 21 | 22 | 0% | 28.83%
2024-04-21 23:00 | 4 | 21 | 23 | 0% | 29.22%
2024-04-22 | 4 | 22 | 0 | 0% | 31.74%
2024-04-22 01:00 | 4 | 22 | 1 | 0% | 29.46%
2024-04-22 02:00 | 4 | 22 | 2 | 0% | 29.72%
2024-04-22 03:00 | 4 | 22 | 3 | 0% | 30.14%
2024-04-22 04:00 | 4 | 22 | 4 | 0% | 29.83%
2024-04-22 05:00 | 4 | 22 | 5 | 2.236% | 28.79%
2024-04-22 06:00 | 4 | 22 | 6 | 12.17% | 26.9%
2024-04-22 07:00 | 4 | 22 | 7 | 33.51% | 24.95%
2024-04-22 08:00 | 4 | 22 | 8 | 54.92% | 23.8%
2024-04-22 09:00 | 4 | 22 | 9 | 70.93% | 22.95%
2024-04-22 10:00 | 4 | 22 | 10 | 75.41% | 22.84%
2024-04-22 11:00 | 4 | 22 | 11 | 75.41% | 22.87%
2024-04-22 12:00 | 4 | 22 | 12 | 75.41% | 23.08%
2024-04-22 13:00 | 4 | 22 | 13 | 75.41% | 25.66%
2024-04-22 14:00 | 4 | 22 | 14 | 74.21% | 23.3%
2024-04-22 15:00 | 4 | 22 | 15 | 59.49% | 22.65%
2024-04-22 16:00 | 4 | 22 | 16 | 38.79% | 22.17%
2024-04-22 17:00 | 4 | 22 | 17 | 16.69% | 21.05%
2024-04-22 18:00 | 4 | 22 | 18 | 3.106% | 20.89%
2024-04-22 19:00 | 4 | 22 | 19 | 0% | 21.26%
2024-04-22 20:00 | 4 | 22 | 20 | 0% | 23.36%
2024-04-22 21:00 | 4 | 22 | 21 | 0% | 25.99%
2024-04-22 22:00 | 4 | 22 | 22 | 0% | 28.54%
2024-04-22 23:00 | 4 | 22 | 23 | 0% | 31.25%
2024-04-23 | 4 | 23 | 0 | 0% | 30.73%
2024-04-23 01:00 | 4 | 23 | 1 | 0% | 32.08%
2024-04-23 02:00 | 4 | 23 | 2 | 0% | 32.23%
2024-04-23 03:00 | 4 | 23 | 3 | 0% | 32.41%
2024-04-23 04:00 | 4 | 23 | 4 | 0% | 32.32%
2024-04-23 05:00 | 4 | 23 | 5 | 2.504% | 30.89%
2024-04-23 06:00 | 4 | 23 | 6 | 13.08% | 28.57%
2024-04-23 07:00 | 4 | 23 | 7 | 34.94% | 26.73%
2024-04-23 08:00 | 4 | 23 | 8 | 56.52% | 26.45%
2024-04-23 09:00 | 4 | 23 | 9 | 72.53% | 26.75%
2024-04-23 10:00 | 4 | 23 | 10 | 75.41% | 27.45%
2024-04-23 11:00 | 4 | 23 | 11 | 75.41% | 28.25%
2024-04-23 12:00 | 4 | 23 | 12 | 75.41% | 29.1%
2024-04-23 13:00 | 4 | 23 | 13 | 75.41% | 30.1%
2024-04-23 14:00 | 4 | 23 | 14 | 75.41% | 30.26%
2024-04-23 15:00 | 4 | 23 | 15 | 60.33% | 30.3%
2024-04-23 16:00 | 4 | 23 | 16 | 39.47% | 30.09%
2024-04-23 17:00 | 4 | 23 | 17 | 17.05% | 29.37%
2024-04-23 18:00 | 4 | 23 | 18 | 3.263% | 27.95%
2024-04-23 19:00 | 4 | 23 | 19 | 0% | 28.17%
2024-04-23 20:00 | 4 | 23 | 20 | 0% | 29.43%
2024-04-23 21:00 | 4 | 23 | 21 | 0% | 31.07%
2024-04-23 22:00 | 4 | 23 | 22 | 0% | 31.19%
2024-04-23 23:00 | 4 | 23 | 23 | 0% | 30.98%
2024-04-24 | 4 | 24 | 0 | 0% | 29.37%
2024-04-24 01:00 | 4 | 24 | 1 | 0% | 30.21%
2024-04-24 02:00 | 4 | 24 | 2 | 0% | 29.84%
2024-04-24 03:00 | 4 | 24 | 3 | 0% | 29.54%
2024-04-24 04:00 | 4 | 24 | 4 | 0% | 28.97%
2024-04-24 05:00 | 4 | 24 | 5 | 2.579% | 28.25%
2024-04-24 06:00 | 4 | 24 | 6 | 11.44% | 26.8%
2024-04-24 07:00 | 4 | 24 | 7 | 28.76% | 25.77%
2024-04-24 08:00 | 4 | 24 | 8 | 48.48% | 26.2%
2024-04-24 09:00 | 4 | 24 | 9 | 71.06% | 26.87%
2024-04-24 10:00 | 4 | 24 | 10 | 75.41% | 28.19%
2024-04-24 11:00 | 4 | 24 | 11 | 75.41% | 29.2%
2024-04-24 12:00 | 4 | 24 | 12 | 75.41% | 26.79%
2024-04-24 13:00 | 4 | 24 | 13 | 75.41% | 31.02%
2024-04-24 14:00 | 4 | 24 | 14 | 74.71% | 31.71%
2024-04-24 15:00 | 4 | 24 | 15 | 59.85% | 30.46%
2024-04-24 16:00 | 4 | 24 | 16 | 39.26% | 29.72%
2024-04-24 17:00 | 4 | 24 | 17 | 17.47% | 28.68%
2024-04-24 18:00 | 4 | 24 | 18 | 3.72% | 27.17%
2024-04-24 19:00 | 4 | 24 | 19 | 0% | 26.77%
2024-04-24 20:00 | 4 | 24 | 20 | 0% | 27.59%
2024-04-24 21:00 | 4 | 24 | 21 | 0% | 28.13%
2024-04-24 22:00 | 4 | 24 | 22 | 0% | 29.07%
2024-04-24 23:00 | 4 | 24 | 23 | 0% | 29.21%
2024-04-25 | 4 | 25 | 0 | 0% | 24.83%
2024-04-25 01:00 | 4 | 25 | 1 | 0% | 29.54%
2024-04-25 02:00 | 4 | 25 | 2 | 0% | 29.37%
2024-04-25 03:00 | 4 | 25 | 3 | 0% | 28.84%
2024-04-25 04:00 | 4 | 25 | 4 | 0% | 28.04%
2024-04-25 05:00 | 4 | 25 | 5 | 0.7896% | 26.32%
2024-04-25 06:00 | 4 | 25 | 6 | 3.707% | 23.76%
2024-04-25 07:00 | 4 | 25 | 7 | 6.594% | 21.22%
2024-04-25 08:00 | 4 | 25 | 8 | 14.04% | 19.96%
2024-04-25 09:00 | 4 | 25 | 9 | 12.35% | 18.95%
2024-04-25 10:00 | 4 | 25 | 10 | 22.1% | 19.25%
2024-04-25 11:00 | 4 | 25 | 11 | 28.83% | 19.79%
2024-04-25 12:00 | 4 | 25 | 12 | 35.05% | 21.07%
2024-04-25 13:00 | 4 | 25 | 13 | 63.34% | 21.83%
2024-04-25 14:00 | 4 | 25 | 14 | 63.45% | 22.07%
2024-04-25 15:00 | 4 | 25 | 15 | 49.5% | 21.81%
2024-04-25 16:00 | 4 | 25 | 16 | 31.5% | 21.08%
2024-04-25 17:00 | 4 | 25 | 17 | 12.4% | 20.26%
2024-04-25 18:00 | 4 | 25 | 18 | 4.131% | 19.43%
2024-04-25 19:00 | 4 | 25 | 19 | 0% | 19.78%
2024-04-25 20:00 | 4 | 25 | 20 | 0% | 21.19%
2024-04-25 21:00 | 4 | 25 | 21 | 0% | 22.92%
2024-04-25 22:00 | 4 | 25 | 22 | 0% | 23.96%
2024-04-25 23:00 | 4 | 25 | 23 | 0% | 24.58%
2024-04-26 | 4 | 26 | 0 | 0% | 22.7%
2024-04-26 01:00 | 4 | 26 | 1 | 0% | 25.11%
2024-04-26 02:00 | 4 | 26 | 2 | 0% | 25.38%
2024-04-26 03:00 | 4 | 26 | 3 | 0% | 25.38%
2024-04-26 04:00 | 4 | 26 | 4 | 0% | 24.6%
2024-04-26 05:00 | 4 | 26 | 5 | 1.307% | 22.77%
2024-04-26 06:00 | 4 | 26 | 6 | 4.028% | 19.61%
2024-04-26 07:00 | 4 | 26 | 7 | 7.913% | 17.87%
2024-04-26 08:00 | 4 | 26 | 8 | 14.23% | 16.82%
2024-04-26 09:00 | 4 | 26 | 9 | 20.39% | 16.44%
2024-04-26 10:00 | 4 | 26 | 10 | 17.53% | 16.43%
2024-04-26 11:00 | 4 | 26 | 11 | 28.36% | 16.92%
2024-04-26 12:00 | 4 | 26 | 12 | 25.72% | 17.26%
2024-04-26 13:00 | 4 | 26 | 13 | 37.83% | 17.77%
2024-04-26 14:00 | 4 | 26 | 14 | 44.81% | 17.79%
2024-04-26 15:00 | 4 | 26 | 15 | 45.19% | 17.75%
2024-04-26 16:00 | 4 | 26 | 16 | 30.02% | 17.34%
2024-04-26 17:00 | 4 | 26 | 17 | 10.88% | 16.22%
2024-04-26 18:00 | 4 | 26 | 18 | 3.571% | 15.47%
2024-04-26 19:00 | 4 | 26 | 19 | 0% | 15.86%
2024-04-26 20:00 | 4 | 26 | 20 | 0% | 17.67%
2024-04-26 21:00 | 4 | 26 | 21 | 0% | 19.72%
2024-04-26 22:00 | 4 | 26 | 22 | 0% | 20.87%
2024-04-26 23:00 | 4 | 26 | 23 | 0% | 21.13%
2024-04-27 | 4 | 27 | 0 | 0% | 24.76%
2024-04-27 01:00 | 4 | 27 | 1 | 0% | 21.18%
2024-04-27 02:00 | 4 | 27 | 2 | 0% | 22.34%
2024-04-27 03:00 | 4 | 27 | 3 | 0% | 22.37%
2024-04-27 04:00 | 4 | 27 | 4 | 0% | 20.62%
2024-04-27 05:00 | 4 | 27 | 5 | 0.5006% | 19.4%
2024-04-27 06:00 | 4 | 27 | 6 | 1.371% | 16.55%
2024-04-27 07:00 | 4 | 27 | 7 | 10.67% | 14.27%
2024-04-27 08:00 | 4 | 27 | 8 | 12.55% | 13.78%
2024-04-27 09:00 | 4 | 27 | 9 | 17.44% | 14.29%
2024-04-27 10:00 | 4 | 27 | 10 | 14.36% | 15.58%
2024-04-27 11:00 | 4 | 27 | 11 | 16.51% | 15.99%
2024-04-27 12:00 | 4 | 27 | 12 | 21.9% | 17.43%
2024-04-27 13:00 | 4 | 27 | 13 | 29.63% | 18.32%
2024-04-27 14:00 | 4 | 27 | 14 | 38.95% | 18.5%
2024-04-27 15:00 | 4 | 27 | 15 | 31.87% | 19.77%
2024-04-27 16:00 | 4 | 27 | 16 | 30.41% | 19.82%
2024-04-27 17:00 | 4 | 27 | 17 | 11.45% | 19.32%
2024-04-27 18:00 | 4 | 27 | 18 | 3.541% | 19.09%
2024-04-27 19:00 | 4 | 27 | 19 | 0% | 19.86%
2024-04-27 20:00 | 4 | 27 | 20 | 0% | 21.61%
2024-04-27 21:00 | 4 | 27 | 21 | 0% | 23.02%
2024-04-27 22:00 | 4 | 27 | 22 | 0% | 24.88%
2024-04-27 23:00 | 4 | 27 | 23 | 0% | 24.34%
2024-04-28 | 4 | 28 | 0 | 0% | 24.99%
2024-04-28 01:00 | 4 | 28 | 1 | 0% | 25.36%
2024-04-28 02:00 | 4 | 28 | 2 | 0% | 26.16%
2024-04-28 03:00 | 4 | 28 | 3 | 0% | 26.89%
2024-04-28 04:00 | 4 | 28 | 4 | 0% | 28.81%
2024-04-28 05:00 | 4 | 28 | 5 | 1.38% | 26.34%
2024-04-28 06:00 | 4 | 28 | 6 | 6.738% | 24.78%
2024-04-28 07:00 | 4 | 28 | 7 | 11.05% | 23.3%
2024-04-28 08:00 | 4 | 28 | 8 | 50.72% | 23.74%
2024-04-28 09:00 | 4 | 28 | 9 | 65.83% | 24.41%
2024-04-28 10:00 | 4 | 28 | 10 | 75.41% | 25.43%
2024-04-28 11:00 | 4 | 28 | 11 | 75.41% | 26.39%
2024-04-28 12:00 | 4 | 28 | 12 | 75.41% | 27.77%
2024-04-28 13:00 | 4 | 28 | 13 | 75.41% | 28.51%
2024-04-28 14:00 | 4 | 28 | 14 | 68.81% | 29.18%
2024-04-28 15:00 | 4 | 28 | 15 | 53.96% | 28.56%
2024-04-28 16:00 | 4 | 28 | 16 | 27.04% | 31.55%
2024-04-28 17:00 | 4 | 28 | 17 | 12.34% | 27.37%
2024-04-28 18:00 | 4 | 28 | 18 | 4.904% | 29.67%
2024-04-28 19:00 | 4 | 28 | 19 | 0% | 26.15%
2024-04-28 20:00 | 4 | 28 | 20 | 0% | 26.1%
2024-04-28 21:00 | 4 | 28 | 21 | 0% | 25.94%
2024-04-28 22:00 | 4 | 28 | 22 | 0% | 26.88%
2024-04-28 23:00 | 4 | 28 | 23 | 0% | 25.8%
2024-04-29 | 4 | 29 | 0 | 0% | 26.22%
2024-04-29 01:00 | 4 | 29 | 1 | 0% | 25.86%
2024-04-29 02:00 | 4 | 29 | 2 | 0% | 25.17%
2024-04-29 03:00 | 4 | 29 | 3 | 0% | 25.96%
2024-04-29 04:00 | 4 | 29 | 4 | 0% | 24.09%
2024-04-29 05:00 | 4 | 29 | 5 | 3.375% | 23.17%
2024-04-29 06:00 | 4 | 29 | 6 | 11.5% | 20.96%
2024-04-29 07:00 | 4 | 29 | 7 | 30.63% | 19.35%
2024-04-29 08:00 | 4 | 29 | 8 | 53.24% | 20.23%
2024-04-29 09:00 | 4 | 29 | 9 | 68.93% | 20.84%
2024-04-29 10:00 | 4 | 29 | 10 | 75.41% | 23.83%
2024-04-29 11:00 | 4 | 29 | 11 | 75.41% | 22.97%
2024-04-29 12:00 | 4 | 29 | 12 | 75.41% | 23.54%
2024-04-29 13:00 | 4 | 29 | 13 | 36.74% | 24.23%
2024-04-29 14:00 | 4 | 29 | 14 | 62.07% | 25.03%
2024-04-29 15:00 | 4 | 29 | 15 | 52.42% | 25.16%
2024-04-29 16:00 | 4 | 29 | 16 | 38.98% | 26.18%
2024-04-29 17:00 | 4 | 29 | 17 | 15.12% | 22.62%
2024-04-29 18:00 | 4 | 29 | 18 | 4.794% | 21.22%
2024-04-29 19:00 | 4 | 29 | 19 | 0.8188% | 21.83%
2024-04-29 20:00 | 4 | 29 | 20 | 0% | 23.53%
2024-04-29 21:00 | 4 | 29 | 21 | 0% | 24.91%
2024-04-29 22:00 | 4 | 29 | 22 | 0% | 25.61%
2024-04-29 23:00 | 4 | 29 | 23 | 0% | 25.56%
2024-04-30 | 4 | 30 | 0 | 0% | 22.77%
2024-04-30 01:00 | 4 | 30 | 1 | 0% | 26.56%
2024-04-30 02:00 | 4 | 30 | 2 | 0% | 26.85%
2024-04-30 03:00 | 4 | 30 | 3 | 0% | 27.18%
2024-04-30 04:00 | 4 | 30 | 4 | 0% | 27.43%
2024-04-30 05:00 | 4 | 30 | 5 | 2.141% | 26.5%
2024-04-30 06:00 | 4 | 30 | 6 | 10.07% | 23.15%
2024-04-30 07:00 | 4 | 30 | 7 | 9.405% | 21.03%
2024-04-30 08:00 | 4 | 30 | 8 | 20.23% | 20.67%
2024-04-30 09:00 | 4 | 30 | 9 | 45.97% | 21.31%
2024-04-30 10:00 | 4 | 30 | 10 | 57.04% | 22.24%
2024-04-30 11:00 | 4 | 30 | 11 | 53.58% | 23.14%
2024-04-30 12:00 | 4 | 30 | 12 | 29.38% | 24.11%
2024-04-30 13:00 | 4 | 30 | 13 | 17.38% | 25.1%
2024-04-30 14:00 | 4 | 30 | 14 | 21.15% | 25.9%
2024-04-30 15:00 | 4 | 30 | 15 | 19.96% | 26.31%
2024-04-30 16:00 | 4 | 30 | 16 | 10.22% | 25.91%
2024-04-30 17:00 | 4 | 30 | 17 | 8.234% | 24.65%
2024-04-30 18:00 | 4 | 30 | 18 | 4.551% | 24.04%
2024-04-30 19:00 | 4 | 30 | 19 | 0.1838% | 24.24%
2024-04-30 20:00 | 4 | 30 | 20 | 0% | 25.09%
2024-04-30 21:00 | 4 | 30 | 21 | 0% | 25.33%
2024-04-30 22:00 | 4 | 30 | 22 | 0% | 25.16%
2024-04-30 23:00 | 4 | 30 | 23 | 0% | 23.79%
2024-05-01 | 5 | 1 | 0 | 0% | 30.49%
2024-05-01 01:00 | 5 | 1 | 1 | 0% | 21.98%
2024-05-01 02:00 | 5 | 1 | 2 | 0% | 21.63%
2024-05-01 03:00 | 5 | 1 | 3 | 0% | 21.14%
2024-05-01 04:00 | 5 | 1 | 4 | 0% | 20.31%
2024-05-01 05:00 | 5 | 1 | 5 | 3.744% | 18.9%
2024-05-01 06:00 | 5 | 1 | 6 | 15.83% | 17.02%
2024-05-01 07:00 | 5 | 1 | 7 | 37.8% | 14.8%
2024-05-01 08:00 | 5 | 1 | 8 | 58.61% | 14.32%
2024-05-01 09:00 | 5 | 1 | 9 | 74.39% | 14.82%
2024-05-01 10:00 | 5 | 1 | 10 | 75.41% | 15.94%
2024-05-01 11:00 | 5 | 1 | 11 | 75.41% | 17.6%
2024-05-01 12:00 | 5 | 1 | 12 | 75.41% | 20.19%
2024-05-01 13:00 | 5 | 1 | 13 | 75.41% | 20.25%
2024-05-01 14:00 | 5 | 1 | 14 | 75.41% | 21.32%
2024-05-01 15:00 | 5 | 1 | 15 | 62.11% | 22.24%
2024-05-01 16:00 | 5 | 1 | 16 | 41.66% | 22.24%
2024-05-01 17:00 | 5 | 1 | 17 | 19.4% | 21.68%
2024-05-01 18:00 | 5 | 1 | 18 | 4.19% | 23.62%
2024-05-01 19:00 | 5 | 1 | 19 | 0.9993% | 22.65%
2024-05-01 20:00 | 5 | 1 | 20 | 0% | 24.33%
2024-05-01 21:00 | 5 | 1 | 21 | 0% | 26.44%
2024-05-01 22:00 | 5 | 1 | 22 | 0% | 28%
2024-05-01 23:00 | 5 | 1 | 23 | 0% | 29.23%
2024-05-02 | 5 | 2 | 0 | 0% | 27.67%
2024-05-02 01:00 | 5 | 2 | 1 | 0% | 31.15%
2024-05-02 02:00 | 5 | 2 | 2 | 0% | 31.88%
2024-05-02 03:00 | 5 | 2 | 3 | 0% | 32.4%
2024-05-02 04:00 | 5 | 2 | 4 | 0% | 32.62%
2024-05-02 05:00 | 5 | 2 | 5 | 4.166% | 32.04%
2024-05-02 06:00 | 5 | 2 | 6 | 15.21% | 29.73%
2024-05-02 07:00 | 5 | 2 | 7 | 37.99% | 27.23%
2024-05-02 08:00 | 5 | 2 | 8 | 58.35% | 27.34%
2024-05-02 09:00 | 5 | 2 | 9 | 73.76% | 27.77%
2024-05-02 10:00 | 5 | 2 | 10 | 75.41% | 29.28%
2024-05-02 11:00 | 5 | 2 | 11 | 75.41% | 30.87%
2024-05-02 12:00 | 5 | 2 | 12 | 75.41% | 32.38%
2024-05-02 13:00 | 5 | 2 | 13 | 75.41% | 33.29%
2024-05-02 14:00 | 5 | 2 | 14 | 75.41% | 35.02%
2024-05-02 15:00 | 5 | 2 | 15 | 60.98% | 34.2%
2024-05-02 16:00 | 5 | 2 | 16 | 41.02% | 33.47%
2024-05-02 17:00 | 5 | 2 | 17 | 19.27% | 31.51%
2024-05-02 18:00 | 5 | 2 | 18 | 4.246% | 30.89%
2024-05-02 19:00 | 5 | 2 | 19 | 1.363% | 27.89%
2024-05-02 20:00 | 5 | 2 | 20 | 0% | 27.77%
2024-05-02 21:00 | 5 | 2 | 21 | 0% | 28.03%
2024-05-02 22:00 | 5 | 2 | 22 | 0% | 28.25%
2024-05-02 23:00 | 5 | 2 | 23 | 0% | 28.3%
2024-05-03 | 5 | 3 | 0 | 0% | 25.57%
2024-05-03 01:00 | 5 | 3 | 1 | 0% | 26.64%
2024-05-03 02:00 | 5 | 3 | 2 | 0% | 25.79%
2024-05-03 03:00 | 5 | 3 | 3 | 0% | 25.07%
2024-05-03 04:00 | 5 | 3 | 4 | 0% | 24.08%
2024-05-03 05:00 | 5 | 3 | 5 | 4.047% | 21.63%
2024-05-03 06:00 | 5 | 3 | 6 | 11.78% | 18.06%
2024-05-03 07:00 | 5 | 3 | 7 | 29.51% | 14.89%
2024-05-03 08:00 | 5 | 3 | 8 | 49.54% | 13.37%
2024-05-03 09:00 | 5 | 3 | 9 | 61.6% | 13.41%
2024-05-03 10:00 | 5 | 3 | 10 | 75.41% | 13.86%
2024-05-03 11:00 | 5 | 3 | 11 | 70.9% | 14.66%
2024-05-03 12:00 | 5 | 3 | 12 | 72.96% | 15.65%
2024-05-03 13:00 | 5 | 3 | 13 | 75.41% | 16.07%
2024-05-03 14:00 | 5 | 3 | 14 | 73.5% | 17.59%
2024-05-03 15:00 | 5 | 3 | 15 | 49.76% | 16.45%
2024-05-03 16:00 | 5 | 3 | 16 | 40.08% | 16.24%
2024-05-03 17:00 | 5 | 3 | 17 | 16.81% | 15.36%
2024-05-03 18:00 | 5 | 3 | 18 | 4.685% | 14.92%
2024-05-03 19:00 | 5 | 3 | 19 | 1.057% | 16.05%
2024-05-03 20:00 | 5 | 3 | 20 | 0% | 18.29%
2024-05-03 21:00 | 5 | 3 | 21 | 0% | 20.37%
2024-05-03 22:00 | 5 | 3 | 22 | 0% | 22.59%
2024-05-03 23:00 | 5 | 3 | 23 | 0% | 24.44%
2024-05-04 | 5 | 4 | 0 | 0% | 26.07%
2024-05-04 01:00 | 5 | 4 | 1 | 0% | 26.64%
2024-05-04 02:00 | 5 | 4 | 2 | 0% | 27.2%
2024-05-04 03:00 | 5 | 4 | 3 | 0% | 27.81%
2024-05-04 04:00 | 5 | 4 | 4 | 0% | 27.88%
2024-05-04 05:00 | 5 | 4 | 5 | 4.1% | 26.36%
2024-05-04 06:00 | 5 | 4 | 6 | 16.49% | 24.13%
2024-05-04 07:00 | 5 | 4 | 7 | 38.08% | 22.24%
2024-05-04 08:00 | 5 | 4 | 8 | 58.4% | 21.49%
2024-05-04 09:00 | 5 | 4 | 9 | 73.9% | 21.77%
2024-05-04 10:00 | 5 | 4 | 10 | 75.41% | 22.26%
2024-05-04 11:00 | 5 | 4 | 11 | 75.41% | 22.87%
2024-05-04 12:00 | 5 | 4 | 12 | 75.41% | 23.3%
2024-05-04 13:00 | 5 | 4 | 13 | 75.41% | 23.16%
2024-05-04 14:00 | 5 | 4 | 14 | 75.41% | 24.91%
2024-05-04 15:00 | 5 | 4 | 15 | 61.4% | 25.46%
2024-05-04 16:00 | 5 | 4 | 16 | 41.66% | 23.7%
2024-05-04 17:00 | 5 | 4 | 17 | 19.82% | 22.66%
2024-05-04 18:00 | 5 | 4 | 18 | 4.577% | 21.4%
2024-05-04 19:00 | 5 | 4 | 19 | 1.808% | 21.03%
2024-05-04 20:00 | 5 | 4 | 20 | 0% | 22.29%
2024-05-04 21:00 | 5 | 4 | 21 | 0% | 23.41%
2024-05-04 22:00 | 5 | 4 | 22 | 0% | 24.63%
2024-05-04 23:00 | 5 | 4 | 23 | 0% | 25.67%
2024-05-05 | 5 | 5 | 0 | 0% | 36.03%
2024-05-05 01:00 | 5 | 5 | 1 | 0% | 26.16%
2024-05-05 02:00 | 5 | 5 | 2 | 0% | 25.71%
2024-05-05 03:00 | 5 | 5 | 3 | 0% | 24.99%
2024-05-05 04:00 | 5 | 5 | 4 | 0% | 23.4%
2024-05-05 05:00 | 5 | 5 | 5 | 4.762% | 20.85%
2024-05-05 06:00 | 5 | 5 | 6 | 16.83% | 17.6%
2024-05-05 07:00 | 5 | 5 | 7 | 38.28% | 15.43%
2024-05-05 08:00 | 5 | 5 | 8 | 58.38% | 15.61%
2024-05-05 09:00 | 5 | 5 | 9 | 73.47% | 17.2%
2024-05-05 10:00 | 5 | 5 | 10 | 75.41% | 19.16%
2024-05-05 11:00 | 5 | 5 | 11 | 75.41% | 21.36%
2024-05-05 12:00 | 5 | 5 | 12 | 75.41% | 23.55%
2024-05-05 13:00 | 5 | 5 | 13 | 75.41% | 25.51%
2024-05-05 14:00 | 5 | 5 | 14 | 74.72% | 27.12%
2024-05-05 15:00 | 5 | 5 | 15 | 60.38% | 30.4%
2024-05-05 16:00 | 5 | 5 | 16 | 40.97% | 29.46%
2024-05-05 17:00 | 5 | 5 | 17 | 19.7% | 29.62%
2024-05-05 18:00 | 5 | 5 | 18 | 4.363% | 29.71%
2024-05-05 19:00 | 5 | 5 | 19 | 1.612% | 31.02%
2024-05-05 20:00 | 5 | 5 | 20 | 0% | 33.02%
2024-05-05 21:00 | 5 | 5 | 21 | 0% | 35.4%
2024-05-05 22:00 | 5 | 5 | 22 | 0% | 35.97%
2024-05-05 23:00 | 5 | 5 | 23 | 0% | 35.77%
2024-05-06 | 5 | 6 | 0 | 0% | 24.96%
2024-05-06 01:00 | 5 | 6 | 1 | 0% | 36.24%
2024-05-06 02:00 | 5 | 6 | 2 | 0% | 35.77%
2024-05-06 03:00 | 5 | 6 | 3 | 0% | 35.75%
2024-05-06 04:00 | 5 | 6 | 4 | 0% | 35.18%
2024-05-06 05:00 | 5 | 6 | 5 | 4.555% | 32.94%
2024-05-06 06:00 | 5 | 6 | 6 | 16.87% | 29.86%
2024-05-06 07:00 | 5 | 6 | 7 | 38% | 27.47%
2024-05-06 08:00 | 5 | 6 | 8 | 56.99% | 24.54%
2024-05-06 09:00 | 5 | 6 | 9 | 71.87% | 26.54%
2024-05-06 10:00 | 5 | 6 | 10 | 75.41% | 26.11%
2024-05-06 11:00 | 5 | 6 | 11 | 75.41% | 26.37%
2024-05-06 12:00 | 5 | 6 | 12 | 75.41% | 26.08%
2024-05-06 13:00 | 5 | 6 | 13 | 75.41% | 26.13%
2024-05-06 14:00 | 5 | 6 | 14 | 74.08% | 28.06%
2024-05-06 15:00 | 5 | 6 | 15 | 59.97% | 25.36%
2024-05-06 16:00 | 5 | 6 | 16 | 40.75% | 24.29%
2024-05-06 17:00 | 5 | 6 | 17 | 19.61% | 22.54%
2024-05-06 18:00 | 5 | 6 | 18 | 4.576% | 21.2%
2024-05-06 19:00 | 5 | 6 | 19 | 1.992% | 21.44%
2024-05-06 20:00 | 5 | 6 | 20 | 0% | 23.1%
2024-05-06 21:00 | 5 | 6 | 21 | 0% | 24.84%
2024-05-06 22:00 | 5 | 6 | 22 | 0% | 25.05%
2024-05-06 23:00 | 5 | 6 | 23 | 0% | 25.06%
2024-05-07 | 5 | 7 | 0 | 0% | 24.52%
2024-05-07 01:00 | 5 | 7 | 1 | 0% | 24.51%
2024-05-07 02:00 | 5 | 7 | 2 | 0% | 24.27%
2024-05-07 03:00 | 5 | 7 | 3 | 0% | 23.85%
2024-05-07 04:00 | 5 | 7 | 4 | 0.3594% | 22.68%
2024-05-07 05:00 | 5 | 7 | 5 | 1.059% | 19.9%
2024-05-07 06:00 | 5 | 7 | 6 | 5.883% | 16.9%
2024-05-07 07:00 | 5 | 7 | 7 | 24.63% | 14.75%
2024-05-07 08:00 | 5 | 7 | 8 | 41.02% | 13.96%
2024-05-07 09:00 | 5 | 7 | 9 | 60.67% | 13.47%
2024-05-07 10:00 | 5 | 7 | 10 | 43.54% | 13.15%
2024-05-07 11:00 | 5 | 7 | 11 | 37.3% | 13.49%
2024-05-07 12:00 | 5 | 7 | 12 | 46.02% | 14.18%
2024-05-07 13:00 | 5 | 7 | 13 | 35.84% | 14.93%
2024-05-07 14:00 | 5 | 7 | 14 | 32.93% | 15.27%
2024-05-07 15:00 | 5 | 7 | 15 | 30.55% | 15.11%
2024-05-07 16:00 | 5 | 7 | 16 | 15.76% | 14.92%
2024-05-07 17:00 | 5 | 7 | 17 | 8.592% | 14.55%
2024-05-07 18:00 | 5 | 7 | 18 | 4.359% | 14.7%
2024-05-07 19:00 | 5 | 7 | 19 | 1.058% | 15.67%
2024-05-07 20:00 | 5 | 7 | 20 | 0% | 18%
2024-05-07 21:00 | 5 | 7 | 21 | 0% | 20.04%
2024-05-07 22:00 | 5 | 7 | 22 | 0% | 22.1%
2024-05-07 23:00 | 5 | 7 | 23 | 0% | 23.51%
2024-05-08 | 5 | 8 | 0 | 0% | 22.11%
2024-05-08 01:00 | 5 | 8 | 1 | 0% | 24.69%
2024-05-08 02:00 | 5 | 8 | 2 | 0% | 25.03%
2024-05-08 03:00 | 5 | 8 | 3 | 0% | 25.06%
2024-05-08 04:00 | 5 | 8 | 4 | 0.9798% | 24.3%
2024-05-08 05:00 | 5 | 8 | 5 | 4.311% | 22.68%
2024-05-08 06:00 | 5 | 8 | 6 | 17.89% | 21.23%
2024-05-08 07:00 | 5 | 8 | 7 | 40.23% | 19.61%
2024-05-08 08:00 | 5 | 8 | 8 | 48.12% | 19.26%
2024-05-08 09:00 | 5 | 8 | 9 | 68.96% | 19.01%
2024-05-08 10:00 | 5 | 8 | 10 | 43.26% | 19%
2024-05-08 11:00 | 5 | 8 | 11 | 33.75% | 19.31%
2024-05-08 12:00 | 5 | 8 | 12 | 56.03% | 19.54%
2024-05-08 13:00 | 5 | 8 | 13 | 51.33% | 19.59%
2024-05-08 14:00 | 5 | 8 | 14 | 33.84% | 19.83%
2024-05-08 15:00 | 5 | 8 | 15 | 37.01% | 19.64%
2024-05-08 16:00 | 5 | 8 | 16 | 38.41% | 18.69%
2024-05-08 17:00 | 5 | 8 | 17 | 21.43% | 17.41%
2024-05-08 18:00 | 5 | 8 | 18 | 5.104% | 16.03%
2024-05-08 19:00 | 5 | 8 | 19 | 2.656% | 16%
2024-05-08 20:00 | 5 | 8 | 20 | 0% | 17.49%
2024-05-08 21:00 | 5 | 8 | 21 | 0% | 19.51%
2024-05-08 22:00 | 5 | 8 | 22 | 0% | 20.83%
2024-05-08 23:00 | 5 | 8 | 23 | 0% | 21.37%
2024-05-09 | 5 | 9 | 0 | 0% | 29.46%
2024-05-09 01:00 | 5 | 9 | 1 | 0% | 22.98%
2024-05-09 02:00 | 5 | 9 | 2 | 0% | 23.41%
2024-05-09 03:00 | 5 | 9 | 3 | 0% | 23.94%
2024-05-09 04:00 | 5 | 9 | 4 | 1.173% | 23.54%
2024-05-09 05:00 | 5 | 9 | 5 | 5.248% | 21.9%
2024-05-09 06:00 | 5 | 9 | 6 | 11.83% | 19.51%
2024-05-09 07:00 | 5 | 9 | 7 | 24.22% | 17.87%
2024-05-09 08:00 | 5 | 9 | 8 | 46.57% | 18.54%
2024-05-09 09:00 | 5 | 9 | 9 | 50.91% | 20.3%
2024-05-09 10:00 | 5 | 9 | 10 | 75.41% | 22.41%
2024-05-09 11:00 | 5 | 9 | 11 | 44.99% | 23.96%
2024-05-09 12:00 | 5 | 9 | 12 | 71.98% | 25.09%
2024-05-09 13:00 | 5 | 9 | 13 | 75.41% | 26.29%
2024-05-09 14:00 | 5 | 9 | 14 | 61.38% | 27.05%
2024-05-09 15:00 | 5 | 9 | 15 | 57.17% | 30.01%
2024-05-09 16:00 | 5 | 9 | 16 | 31.13% | 27.32%
2024-05-09 17:00 | 5 | 9 | 17 | 13.94% | 27%
2024-05-09 18:00 | 5 | 9 | 18 | 4.526% | 27.01%
2024-05-09 19:00 | 5 | 9 | 19 | 0.7332% | 27.77%
2024-05-09 20:00 | 5 | 9 | 20 | 0% | 29.26%
2024-05-09 21:00 | 5 | 9 | 21 | 0% | 30.29%
2024-05-09 22:00 | 5 | 9 | 22 | 0% | 30.84%
2024-05-09 23:00 | 5 | 9 | 23 | 0% | 32.13%
2024-05-10 | 5 | 10 | 0 | 0% | 30.35%
2024-05-10 01:00 | 5 | 10 | 1 | 0% | 28.9%
2024-05-10 02:00 | 5 | 10 | 2 | 0% | 28.52%
2024-05-10 03:00 | 5 | 10 | 3 | 0% | 28.29%
2024-05-10 04:00 | 5 | 10 | 4 | 0.5608% | 26.91%
2024-05-10 05:00 | 5 | 10 | 5 | 1.738% | 24.9%
2024-05-10 06:00 | 5 | 10 | 6 | 6.95% | 21.79%
2024-05-10 07:00 | 5 | 10 | 7 | 22.66% | 19.02%
2024-05-10 08:00 | 5 | 10 | 8 | 21.36% | 18.02%
2024-05-10 09:00 | 5 | 10 | 9 | 28.14% | 18.02%
2024-05-10 10:00 | 5 | 10 | 10 | 36.03% | 18.8%
2024-05-10 11:00 | 5 | 10 | 11 | 32.07% | 19.95%
2024-05-10 12:00 | 5 | 10 | 12 | 36.27% | 23.1%
2024-05-10 13:00 | 5 | 10 | 13 | 33.95% | 22.54%
2024-05-10 14:00 | 5 | 10 | 14 | 28.23% | 23.54%
2024-05-10 15:00 | 5 | 10 | 15 | 24.46% | 23.87%
2024-05-10 16:00 | 5 | 10 | 16 | 16.11% | 24.44%
2024-05-10 17:00 | 5 | 10 | 17 | 10.32% | 24.28%
2024-05-10 18:00 | 5 | 10 | 18 | 5.536% | 24.62%
2024-05-10 19:00 | 5 | 10 | 19 | 1.095% | 25.37%
2024-05-10 20:00 | 5 | 10 | 20 | 0% | 27.42%
2024-05-10 21:00 | 5 | 10 | 21 | 0% | 28.94%
2024-05-10 22:00 | 5 | 10 | 22 | 0% | 29.76%
2024-05-10 23:00 | 5 | 10 | 23 | 0% | 30.34%
2024-05-11 | 5 | 11 | 0 | 0% | 26.56%
2024-05-11 01:00 | 5 | 11 | 1 | 0% | 29.48%
2024-05-11 02:00 | 5 | 11 | 2 | 0% | 28.26%
2024-05-11 03:00 | 5 | 11 | 3 | 0% | 26.23%
2024-05-11 04:00 | 5 | 11 | 4 | 0% | 24.37%
2024-05-11 05:00 | 5 | 11 | 5 | 0.8171% | 21.73%
2024-05-11 06:00 | 5 | 11 | 6 | 4.12% | 19.03%
2024-05-11 07:00 | 5 | 11 | 7 | 8.756% | 16.84%
2024-05-11 08:00 | 5 | 11 | 8 | 12.84% | 16.12%
2024-05-11 09:00 | 5 | 11 | 9 | 17.19% | 16.38%
2024-05-11 10:00 | 5 | 11 | 10 | 17.37% | 18.47%
2024-05-11 11:00 | 5 | 11 | 11 | 20.15% | 18.77%
2024-05-11 12:00 | 5 | 11 | 12 | 23.7% | 19.04%
2024-05-11 13:00 | 5 | 11 | 13 | 23.93% | 19.04%
2024-05-11 14:00 | 5 | 11 | 14 | 21.72% | 18.92%
2024-05-11 15:00 | 5 | 11 | 15 | 20.42% | 19.04%
2024-05-11 16:00 | 5 | 11 | 16 | 16.33% | 18.84%
2024-05-11 17:00 | 5 | 11 | 17 | 11.31% | 18.79%
2024-05-11 18:00 | 5 | 11 | 18 | 5.527% | 19.32%
2024-05-11 19:00 | 5 | 11 | 19 | 1.794% | 20.75%
2024-05-11 20:00 | 5 | 11 | 20 | 0% | 23.2%
2024-05-11 21:00 | 5 | 11 | 21 | 0% | 25.69%
2024-05-11 22:00 | 5 | 11 | 22 | 0% | 26.94%
2024-05-11 23:00 | 5 | 11 | 23 | 0% | 27.01%
2024-05-12 | 5 | 12 | 0 | 0% | 26.15%
2024-05-12 01:00 | 5 | 12 | 1 | 0% | 28.39%
2024-05-12 02:00 | 5 | 12 | 2 | 0% | 25.82%
2024-05-12 03:00 | 5 | 12 | 3 | 0% | 25.03%
2024-05-12 04:00 | 5 | 12 | 4 | 0.7837% | 24.02%
2024-05-12 05:00 | 5 | 12 | 5 | 1.906% | 22.57%
2024-05-12 06:00 | 5 | 12 | 6 | 11.77% | 20.4%
2024-05-12 07:00 | 5 | 12 | 7 | 33.45% | 18.8%
2024-05-12 08:00 | 5 | 12 | 8 | 58.97% | 18.52%
2024-05-12 09:00 | 5 | 12 | 9 | 73.98% | 19.15%
2024-05-12 10:00 | 5 | 12 | 10 | 75.41% | 19.76%
2024-05-12 11:00 | 5 | 12 | 11 | 75.41% | 20.14%
2024-05-12 12:00 | 5 | 12 | 12 | 75.41% | 20.5%
2024-05-12 13:00 | 5 | 12 | 13 | 75.41% | 20.53%
2024-05-12 14:00 | 5 | 12 | 14 | 75.41% | 19.56%
2024-05-12 15:00 | 5 | 12 | 15 | 62.36% | 20.47%
2024-05-12 16:00 | 5 | 12 | 16 | 43.08% | 20.27%
2024-05-12 17:00 | 5 | 12 | 17 | 21.74% | 18.96%
2024-05-12 18:00 | 5 | 12 | 18 | 5.318% | 20.06%
2024-05-12 19:00 | 5 | 12 | 19 | 2.865% | 21.91%
2024-05-12 20:00 | 5 | 12 | 20 | 0% | 24.18%
2024-05-12 21:00 | 5 | 12 | 21 | 0% | 25.9%
2024-05-12 22:00 | 5 | 12 | 22 | 0% | 26.79%
2024-05-12 23:00 | 5 | 12 | 23 | 0% | 28.09%
2024-05-13 | 5 | 13 | 0 | 0% | 25.16%
2024-05-13 01:00 | 5 | 13 | 1 | 0% | 23.59%
2024-05-13 02:00 | 5 | 13 | 2 | 0% | 24.45%
2024-05-13 03:00 | 5 | 13 | 3 | 0% | 23.79%
2024-05-13 04:00 | 5 | 13 | 4 | 0.4611% | 22.49%
2024-05-13 05:00 | 5 | 13 | 5 | 2.433% | 20.39%
2024-05-13 06:00 | 5 | 13 | 6 | 2.225% | 18.12%
2024-05-13 07:00 | 5 | 13 | 7 | 5.607% | 16.35%
2024-05-13 08:00 | 5 | 13 | 8 | 15.72% | 15.57%
2024-05-13 09:00 | 5 | 13 | 9 | 19.4% | 15.85%
2024-05-13 10:00 | 5 | 13 | 10 | 19.16% | 15.98%
2024-05-13 11:00 | 5 | 13 | 11 | 14.14% | 16.32%
2024-05-13 12:00 | 5 | 13 | 12 | 10.99% | 16.87%
2024-05-13 13:00 | 5 | 13 | 13 | 10.78% | 17.16%
2024-05-13 14:00 | 5 | 13 | 14 | 9.57% | 17.19%
2024-05-13 15:00 | 5 | 13 | 15 | 13.45% | 17.27%
2024-05-13 16:00 | 5 | 13 | 16 | 17.35% | 17.58%
2024-05-13 17:00 | 5 | 13 | 17 | 10.97% | 17.15%
2024-05-13 18:00 | 5 | 13 | 18 | 5.963% | 17.34%
2024-05-13 19:00 | 5 | 13 | 19 | 1.229% | 18.54%
2024-05-13 20:00 | 5 | 13 | 20 | 0% | 21.87%
2024-05-13 21:00 | 5 | 13 | 21 | 0% | 22.82%
2024-05-13 22:00 | 5 | 13 | 22 | 0% | 23.62%
2024-05-13 23:00 | 5 | 13 | 23 | 0% | 24.36%
2024-05-14 | 5 | 14 | 0 | 0% | 27.3%
2024-05-14 01:00 | 5 | 14 | 1 | 0% | 24.84%
2024-05-14 02:00 | 5 | 14 | 2 | 0% | 24.35%
2024-05-14 03:00 | 5 | 14 | 3 | 0% | 24.22%
2024-05-14 04:00 | 5 | 14 | 4 | 0.1878% | 23.3%
2024-05-14 05:00 | 5 | 14 | 5 | 0.6041% | 22.06%
2024-05-14 06:00 | 5 | 14 | 6 | 4.381% | 20.23%
2024-05-14 07:00 | 5 | 14 | 7 | 6.643% | 18.33%
2024-05-14 08:00 | 5 | 14 | 8 | 11.15% | 17.26%
2024-05-14 09:00 | 5 | 14 | 9 | 22.7% | 16.8%
2024-05-14 10:00 | 5 | 14 | 10 | 52.31% | 16.38%
2024-05-14 11:00 | 5 | 14 | 11 | 75.41% | 17.67%
2024-05-14 12:00 | 5 | 14 | 12 | 68.23% | 18.95%
2024-05-14 13:00 | 5 | 14 | 13 | 26.03% | 19.9%
2024-05-14 14:00 | 5 | 14 | 14 | 40.57% | 20.75%
2024-05-14 15:00 | 5 | 14 | 15 | 32.14% | 22.27%
2024-05-14 16:00 | 5 | 14 | 16 | 30.73% | 22.21%
2024-05-14 17:00 | 5 | 14 | 17 | 12.38% | 21.49%
2024-05-14 18:00 | 5 | 14 | 18 | 6.168% | 21.46%
2024-05-14 19:00 | 5 | 14 | 19 | 2.398% | 21.58%
2024-05-14 20:00 | 5 | 14 | 20 | 0% | 22.79%
2024-05-14 21:00 | 5 | 14 | 21 | 0% | 24.31%
2024-05-14 22:00 | 5 | 14 | 22 | 0% | 26.28%
2024-05-14 23:00 | 5 | 14 | 23 | 0% | 26.64%
2024-05-15 | 5 | 15 | 0 | 0% | 26.06%
2024-05-15 01:00 | 5 | 15 | 1 | 0% | 27.24%
2024-05-15 02:00 | 5 | 15 | 2 | 0% | 26.9%
2024-05-15 03:00 | 5 | 15 | 3 | 0% | 26.01%
2024-05-15 04:00 | 5 | 15 | 4 | 0.8041% | 25.15%
2024-05-15 05:00 | 5 | 15 | 5 | 3.432% | 24.81%
2024-05-15 06:00 | 5 | 15 | 6 | 6.218% | 21.19%
2024-05-15 07:00 | 5 | 15 | 7 | 17.36% | 19.32%
2024-05-15 08:00 | 5 | 15 | 8 | 25.83% | 18.79%
2024-05-15 09:00 | 5 | 15 | 9 | 35.81% | 18.49%
2024-05-15 10:00 | 5 | 15 | 10 | 19.2% | 18.4%
2024-05-15 11:00 | 5 | 15 | 11 | 33.77% | 18.42%
2024-05-15 12:00 | 5 | 15 | 12 | 32.66% | 18.41%
2024-05-15 13:00 | 5 | 15 | 13 | 25.51% | 18.61%
2024-05-15 14:00 | 5 | 15 | 14 | 25.65% | 18.81%
2024-05-15 15:00 | 5 | 15 | 15 | 50.75% | 19.36%
2024-05-15 16:00 | 5 | 15 | 16 | 42.84% | 18.54%
2024-05-15 17:00 | 5 | 15 | 17 | 22.14% | 18.72%
2024-05-15 18:00 | 5 | 15 | 18 | 6.15% | 17.17%
2024-05-15 19:00 | 5 | 15 | 19 | 2.294% | 18.91%
2024-05-15 20:00 | 5 | 15 | 20 | 0% | 20.59%
2024-05-15 21:00 | 5 | 15 | 21 | 0% | 22.77%
2024-05-15 22:00 | 5 | 15 | 22 | 0% | 24.8%
2024-05-15 23:00 | 5 | 15 | 23 | 0% | 25.89%
2024-05-16 | 5 | 16 | 0 | 0% | 33.17%
2024-05-16 01:00 | 5 | 16 | 1 | 0% | 26.62%
2024-05-16 02:00 | 5 | 16 | 2 | 0% | 26.85%
2024-05-16 03:00 | 5 | 16 | 3 | 0% | 26.57%
2024-05-16 04:00 | 5 | 16 | 4 | 0.7169% | 26.35%
2024-05-16 05:00 | 5 | 16 | 5 | 2.667% | 24.49%
2024-05-16 06:00 | 5 | 16 | 6 | 10.24% | 22.45%
2024-05-16 07:00 | 5 | 16 | 7 | 11.32% | 21.74%
2024-05-16 08:00 | 5 | 16 | 8 | 15.35% | 20.34%
2024-05-16 09:00 | 5 | 16 | 9 | 29.66% | 20.69%
2024-05-16 10:00 | 5 | 16 | 10 | 23.95% | 21.68%
2024-05-16 11:00 | 5 | 16 | 11 | 28.43% | 22.68%
2024-05-16 12:00 | 5 | 16 | 12 | 28.31% | 23.22%
2024-05-16 13:00 | 5 | 16 | 13 | 28.88% | 23.67%
2024-05-16 14:00 | 5 | 16 | 14 | 18.38% | 23.66%
2024-05-16 15:00 | 5 | 16 | 15 | 13.08% | 24.25%
2024-05-16 16:00 | 5 | 16 | 16 | 9.014% | 25.24%
2024-05-16 17:00 | 5 | 16 | 17 | 9.441% | 24.46%
2024-05-16 18:00 | 5 | 16 | 18 | 4.34% | 24.45%
2024-05-16 19:00 | 5 | 16 | 19 | 1.335% | 26.09%
2024-05-16 20:00 | 5 | 16 | 20 | 0% | 28.29%
2024-05-16 21:00 | 5 | 16 | 21 | 0% | 29.7%
2024-05-16 22:00 | 5 | 16 | 22 | 0% | 31%
2024-05-16 23:00 | 5 | 16 | 23 | 0% | 32.31%
2024-05-17 | 5 | 17 | 0 | 0% | 30.65%
2024-05-17 01:00 | 5 | 17 | 1 | 0% | 34.26%
2024-05-17 02:00 | 5 | 17 | 2 | 0% | 35.41%
2024-05-17 03:00 | 5 | 17 | 3 | 0% | 36.82%
2024-05-17 04:00 | 5 | 17 | 4 | 0% | 37.88%
2024-05-17 05:00 | 5 | 17 | 5 | 0% | 36.13%
2024-05-17 06:00 | 5 | 17 | 6 | 0.5491% | 34.13%
2024-05-17 07:00 | 5 | 17 | 7 | 5.001% | 31.77%
2024-05-17 08:00 | 5 | 17 | 8 | 11.67% | 30.85%
2024-05-17 09:00 | 5 | 17 | 9 | 21.74% | 31.11%
2024-05-17 10:00 | 5 | 17 | 10 | 24.1% | 30.1%
2024-05-17 11:00 | 5 | 17 | 11 | 20.71% | 29.69%
2024-05-17 12:00 | 5 | 17 | 12 | 21.07% | 31.26%
2024-05-17 13:00 | 5 | 17 | 13 | 22.57% | 28.75%
2024-05-17 14:00 | 5 | 17 | 14 | 19.41% | 27.43%
2024-05-17 15:00 | 5 | 17 | 15 | 15.21% | 27.18%
2024-05-17 16:00 | 5 | 17 | 16 | 10.2% | 26.76%
2024-05-17 17:00 | 5 | 17 | 17 | 9.2% | 26.03%
2024-05-17 18:00 | 5 | 17 | 18 | 6.732% | 24.15%
2024-05-17 19:00 | 5 | 17 | 19 | 2.323% | 23.68%
2024-05-17 20:00 | 5 | 17 | 20 | 0% | 25.28%
2024-05-17 21:00 | 5 | 17 | 21 | 0% | 26.87%
2024-05-17 22:00 | 5 | 17 | 22 | 0% | 28.32%
2024-05-17 23:00 | 5 | 17 | 23 | 0% | 29.42%
2024-05-18 | 5 | 18 | 0 | 0% | 21.96%
2024-05-18 01:00 | 5 | 18 | 1 | 0% | 30.81%
2024-05-18 02:00 | 5 | 18 | 2 | 0% | 30.41%
2024-05-18 03:00 | 5 | 18 | 3 | 0% | 30.19%
2024-05-18 04:00 | 5 | 18 | 4 | 1.761% | 29.02%
2024-05-18 05:00 | 5 | 18 | 5 | 6.27% | 25.95%
2024-05-18 06:00 | 5 | 18 | 6 | 16.14% | 22.58%
2024-05-18 07:00 | 5 | 18 | 7 | 37.72% | 19.9%
2024-05-18 08:00 | 5 | 18 | 8 | 55.53% | 19.32%
2024-05-18 09:00 | 5 | 18 | 9 | 69.66% | 18.61%
2024-05-18 10:00 | 5 | 18 | 10 | 75.41% | 18.87%
2024-05-18 11:00 | 5 | 18 | 11 | 75.41% | 19.14%
2024-05-18 12:00 | 5 | 18 | 12 | 75.41% | 18.84%
2024-05-18 13:00 | 5 | 18 | 13 | 75.41% | 19.12%
2024-05-18 14:00 | 5 | 18 | 14 | 71.46% | 20.88%
2024-05-18 15:00 | 5 | 18 | 15 | 58.03% | 20.96%
2024-05-18 16:00 | 5 | 18 | 16 | 37.25% | 21.19%
2024-05-18 17:00 | 5 | 18 | 17 | 17.28% | 21.18%
2024-05-18 18:00 | 5 | 18 | 18 | 6.979% | 19.61%
2024-05-18 19:00 | 5 | 18 | 19 | 1.546% | 19.8%
2024-05-18 20:00 | 5 | 18 | 20 | 0% | 20.97%
2024-05-18 21:00 | 5 | 18 | 21 | 0% | 22.19%
2024-05-18 22:00 | 5 | 18 | 22 | 0% | 22.85%
2024-05-18 23:00 | 5 | 18 | 23 | 0% | 22.27%
2024-05-19 | 5 | 19 | 0 | 0% | 22.78%
2024-05-19 01:00 | 5 | 19 | 1 | 0% | 21.84%
2024-05-19 02:00 | 5 | 19 | 2 | 0% | 20.99%
2024-05-19 03:00 | 5 | 19 | 3 | 0% | 20.1%
2024-05-19 04:00 | 5 | 19 | 4 | 0.1868% | 18.63%
2024-05-19 05:00 | 5 | 19 | 5 | 3.825% | 15.79%
2024-05-19 06:00 | 5 | 19 | 6 | 15.2% | 11.82%
2024-05-19 07:00 | 5 | 19 | 7 | 33.87% | 9.281%
2024-05-19 08:00 | 5 | 19 | 8 | 49.42% | 7.908%
2024-05-19 09:00 | 5 | 19 | 9 | 56.71% | 7.816%
2024-05-19 10:00 | 5 | 19 | 10 | 58.28% | 8.533%
2024-05-19 11:00 | 5 | 19 | 11 | 75.41% | 8.575%
2024-05-19 12:00 | 5 | 19 | 12 | 67.79% | 9.331%
2024-05-19 13:00 | 5 | 19 | 13 | 46.07% | 10.28%
2024-05-19 14:00 | 5 | 19 | 14 | 50.81% | 11.05%
2024-05-19 15:00 | 5 | 19 | 15 | 45.21% | 12.06%
2024-05-19 16:00 | 5 | 19 | 16 | 19.15% | 12.77%
2024-05-19 17:00 | 5 | 19 | 17 | 15.89% | 12.66%
2024-05-19 18:00 | 5 | 19 | 18 | 6.412% | 12.85%
2024-05-19 19:00 | 5 | 19 | 19 | 2.768% | 14.32%
2024-05-19 20:00 | 5 | 19 | 20 | 0% | 16.88%
2024-05-19 21:00 | 5 | 19 | 21 | 0% | 19.02%
2024-05-19 22:00 | 5 | 19 | 22 | 0% | 20.89%
2024-05-19 23:00 | 5 | 19 | 23 | 0% | 22.16%
2024-05-20 | 5 | 20 | 0 | 0% | 20.96%
2024-05-20 01:00 | 5 | 20 | 1 | 0% | 23.1%
2024-05-20 02:00 | 5 | 20 | 2 | 0% | 23.61%
2024-05-20 03:00 | 5 | 20 | 3 | 0% | 23.86%
2024-05-20 04:00 | 5 | 20 | 4 | 1.774% | 23.52%
2024-05-20 05:00 | 5 | 20 | 5 | 6.518% | 21.09%
2024-05-20 06:00 | 5 | 20 | 6 | 16.76% | 18.4%
2024-05-20 07:00 | 5 | 20 | 7 | 35.93% | 16.48%
2024-05-20 08:00 | 5 | 20 | 8 | 52.03% | 15.03%
2024-05-20 09:00 | 5 | 20 | 9 | 63.49% | 14.23%
2024-05-20 10:00 | 5 | 20 | 10 | 75.41% | 14%
2024-05-20 11:00 | 5 | 20 | 11 | 73.74% | 14.09%
2024-05-20 12:00 | 5 | 20 | 12 | 44.21% | 14.4%
2024-05-20 13:00 | 5 | 20 | 13 | 28.92% | 14.42%
2024-05-20 14:00 | 5 | 20 | 14 | 23.66% | 14.76%
2024-05-20 15:00 | 5 | 20 | 15 | 19.29% | 14.84%
2024-05-20 16:00 | 5 | 20 | 16 | 10.67% | 14.9%
2024-05-20 17:00 | 5 | 20 | 17 | 10.18% | 14.67%
2024-05-20 18:00 | 5 | 20 | 18 | 6.443% | 14.49%
2024-05-20 19:00 | 5 | 20 | 19 | 2.276% | 15.55%
2024-05-20 20:00 | 5 | 20 | 20 | 0% | 18.12%
2024-05-20 21:00 | 5 | 20 | 21 | 0% | 20.04%
2024-05-20 22:00 | 5 | 20 | 22 | 0% | 20.93%
2024-05-20 23:00 | 5 | 20 | 23 | 0% | 21.29%
2024-05-21 | 5 | 21 | 0 | 0% | 23.53%
2024-05-21 01:00 | 5 | 21 | 1 | 0% | 20.34%
2024-05-21 02:00 | 5 | 21 | 2 | 0% | 19.96%
2024-05-21 03:00 | 5 | 21 | 3 | 0% | 19.32%
2024-05-21 04:00 | 5 | 21 | 4 | 2.222% | 18.22%
2024-05-21 05:00 | 5 | 21 | 5 | 6.664% | 15.97%
2024-05-21 06:00 | 5 | 21 | 6 | 17.46% | 13.75%
2024-05-21 07:00 | 5 | 21 | 7 | 33.52% | 12.25%
2024-05-21 08:00 | 5 | 21 | 8 | 39.75% | 11.83%
2024-05-21 09:00 | 5 | 21 | 9 | 69.68% | 12%
2024-05-21 10:00 | 5 | 21 | 10 | 75.41% | 12.41%
2024-05-21 11:00 | 5 | 21 | 11 | 75.41% | 13.31%
2024-05-21 12:00 | 5 | 21 | 12 | 75.41% | 13.9%
2024-05-21 13:00 | 5 | 21 | 13 | 75.41% | 14.35%
2024-05-21 14:00 | 5 | 21 | 14 | 75.41% | 15.03%
2024-05-21 15:00 | 5 | 21 | 15 | 62.28% | 15.89%
2024-05-21 16:00 | 5 | 21 | 16 | 43.82% | 16.73%
2024-05-21 17:00 | 5 | 21 | 17 | 23.36% | 16.75%
2024-05-21 18:00 | 5 | 21 | 18 | 6.798% | 16.94%
2024-05-21 19:00 | 5 | 21 | 19 | 3.389% | 17.48%
2024-05-21 20:00 | 5 | 21 | 20 | 0% | 19.22%
2024-05-21 21:00 | 5 | 21 | 21 | 0% | 21.24%
2024-05-21 22:00 | 5 | 21 | 22 | 0% | 22.72%
2024-05-21 23:00 | 5 | 21 | 23 | 0% | 23.43%
2024-05-22 | 5 | 22 | 0 | 0% | 32.82%
2024-05-22 01:00 | 5 | 22 | 1 | 0% | 23.49%
2024-05-22 02:00 | 5 | 22 | 2 | 0% | 23.32%
2024-05-22 03:00 | 5 | 22 | 3 | 0% | 23.04%
2024-05-22 04:00 | 5 | 22 | 4 | 1.521% | 22.39%
2024-05-22 05:00 | 5 | 22 | 5 | 7.339% | 20.82%
2024-05-22 06:00 | 5 | 22 | 6 | 15.77% | 18.99%
2024-05-22 07:00 | 5 | 22 | 7 | 21.94% | 18.3%
2024-05-22 08:00 | 5 | 22 | 8 | 32.06% | 18.36%
2024-05-22 09:00 | 5 | 22 | 9 | 50.9% | 18.95%
2024-05-22 10:00 | 5 | 22 | 10 | 61.03% | 19.64%
2024-05-22 11:00 | 5 | 22 | 11 | 75.41% | 20.86%
2024-05-22 12:00 | 5 | 22 | 12 | 75.41% | 21.69%
2024-05-22 13:00 | 5 | 22 | 13 | 75.41% | 22.8%
2024-05-22 14:00 | 5 | 22 | 14 | 71.8% | 23.63%
2024-05-22 15:00 | 5 | 22 | 15 | 56.71% | 24.2%
2024-05-22 16:00 | 5 | 22 | 16 | 44.03% | 25.16%
2024-05-22 17:00 | 5 | 22 | 17 | 17.57% | 25.3%
2024-05-22 18:00 | 5 | 22 | 18 | 8.681% | 25.85%
2024-05-22 19:00 | 5 | 22 | 19 | 3.506% | 26.97%
2024-05-22 20:00 | 5 | 22 | 20 | 0% | 28.21%
2024-05-22 21:00 | 5 | 22 | 21 | 0% | 29.86%
2024-05-22 22:00 | 5 | 22 | 22 | 0% | 31.17%
2024-05-22 23:00 | 5 | 22 | 23 | 0% | 31.17%
2024-05-23 | 5 | 23 | 0 | 0% | 21.74%
2024-05-23 01:00 | 5 | 23 | 1 | 0% | 30.69%
2024-05-23 02:00 | 5 | 23 | 2 | 0% | 30.4%
2024-05-23 03:00 | 5 | 23 | 3 | 0% | 29.82%
2024-05-23 04:00 | 5 | 23 | 4 | 1.62% | 28.58%
2024-05-23 05:00 | 5 | 23 | 5 | 6.317% | 25.87%
2024-05-23 06:00 | 5 | 23 | 6 | 18.22% | 22.69%
2024-05-23 07:00 | 5 | 23 | 7 | 40.85% | 20.46%
2024-05-23 08:00 | 5 | 23 | 8 | 59.07% | 19.46%
2024-05-23 09:00 | 5 | 23 | 9 | 73.34% | 19.05%
2024-05-23 10:00 | 5 | 23 | 10 | 75.41% | 19.44%
2024-05-23 11:00 | 5 | 23 | 11 | 75.41% | 20.13%
2024-05-23 12:00 | 5 | 23 | 12 | 75.41% | 20.25%
2024-05-23 13:00 | 5 | 23 | 13 | 75.41% | 21.45%
2024-05-23 14:00 | 5 | 23 | 14 | 74.93% | 19.45%
2024-05-23 15:00 | 5 | 23 | 15 | 61.58% | 18.71%
2024-05-23 16:00 | 5 | 23 | 16 | 40.11% | 18.89%
2024-05-23 17:00 | 5 | 23 | 17 | 18.75% | 17.89%
2024-05-23 18:00 | 5 | 23 | 18 | 8.327% | 17.09%
2024-05-23 19:00 | 5 | 23 | 19 | 3.252% | 17.21%
2024-05-23 20:00 | 5 | 23 | 20 | 0% | 18.67%
2024-05-23 21:00 | 5 | 23 | 21 | 0% | 20.46%
2024-05-23 22:00 | 5 | 23 | 22 | 0% | 21.5%
2024-05-23 23:00 | 5 | 23 | 23 | 0% | 22.11%
2024-05-24 | 5 | 24 | 0 | 0% | 24.03%
2024-05-24 01:00 | 5 | 24 | 1 | 0% | 21.45%
2024-05-24 02:00 | 5 | 24 | 2 | 0% | 21.15%
2024-05-24 03:00 | 5 | 24 | 3 | 0% | 22.3%
2024-05-24 04:00 | 5 | 24 | 4 | 0.6335% | 19.7%
2024-05-24 05:00 | 5 | 24 | 5 | 0.5961% | 18.05%
2024-05-24 06:00 | 5 | 24 | 6 | 2.368% | 16.81%
2024-05-24 07:00 | 5 | 24 | 7 | 3.703% | 16.66%
2024-05-24 08:00 | 5 | 24 | 8 | 13.38% | 17.87%
2024-05-24 09:00 | 5 | 24 | 9 | 32.89% | 19.29%
2024-05-24 10:00 | 5 | 24 | 10 | 58.95% | 21.04%
2024-05-24 11:00 | 5 | 24 | 11 | 75.41% | 22.54%
2024-05-24 12:00 | 5 | 24 | 12 | 75.41% | 23.54%
2024-05-24 13:00 | 5 | 24 | 13 | 75.41% | 23.76%
2024-05-24 14:00 | 5 | 24 | 14 | 75.01% | 25.59%
2024-05-24 15:00 | 5 | 24 | 15 | 61.64% | 23.71%
2024-05-24 16:00 | 5 | 24 | 16 | 43.6% | 23.35%
2024-05-24 17:00 | 5 | 24 | 17 | 20.62% | 21.94%
2024-05-24 18:00 | 5 | 24 | 18 | 7.924% | 21.09%
2024-05-24 19:00 | 5 | 24 | 19 | 3.24% | 20.72%
2024-05-24 20:00 | 5 | 24 | 20 | 0% | 21.62%
2024-05-24 21:00 | 5 | 24 | 21 | 0% | 23.19%
2024-05-24 22:00 | 5 | 24 | 22 | 0% | 23.87%
2024-05-24 23:00 | 5 | 24 | 23 | 0% | 24.23%
2024-05-25 | 5 | 25 | 0 | 0% | 32.26%
2024-05-25 01:00 | 5 | 25 | 1 | 0% | 23.36%
2024-05-25 02:00 | 5 | 25 | 2 | 0% | 22.99%
2024-05-25 03:00 | 5 | 25 | 3 | 0% | 22.62%
2024-05-25 04:00 | 5 | 25 | 4 | 2.734% | 21.04%
2024-05-25 05:00 | 5 | 25 | 5 | 6.599% | 18.97%
2024-05-25 06:00 | 5 | 25 | 6 | 18.86% | 17.52%
2024-05-25 07:00 | 5 | 25 | 7 | 37.66% | 16.83%
2024-05-25 08:00 | 5 | 25 | 8 | 58.82% | 17.1%
2024-05-25 09:00 | 5 | 25 | 9 | 72.72% | 18.06%
2024-05-25 10:00 | 5 | 25 | 10 | 75.41% | 19.48%
2024-05-25 11:00 | 5 | 25 | 11 | 75.41% | 21.57%
2024-05-25 12:00 | 5 | 25 | 12 | 75.41% | 22.56%
2024-05-25 13:00 | 5 | 25 | 13 | 75.41% | 23.98%
2024-05-25 14:00 | 5 | 25 | 14 | 74.37% | 25.35%
2024-05-25 15:00 | 5 | 25 | 15 | 61.67% | 26.55%
2024-05-25 16:00 | 5 | 25 | 16 | 43.63% | 27.3%
2024-05-25 17:00 | 5 | 25 | 17 | 23.53% | 27.03%
2024-05-25 18:00 | 5 | 25 | 18 | 7.442% | 29.52%
2024-05-25 19:00 | 5 | 25 | 19 | 3.627% | 27.4%
2024-05-25 20:00 | 5 | 25 | 20 | 0% | 29.19%
2024-05-25 21:00 | 5 | 25 | 21 | 0% | 30.88%
2024-05-25 22:00 | 5 | 25 | 22 | 0% | 32.04%
2024-05-25 23:00 | 5 | 25 | 23 | 0% | 32.22%
2024-05-26 | 5 | 26 | 0 | 0% | 29.56%
2024-05-26 01:00 | 5 | 26 | 1 | 0% | 32.01%
2024-05-26 02:00 | 5 | 26 | 2 | 0% | 31.95%
2024-05-26 03:00 | 5 | 26 | 3 | 0% | 31.5%
2024-05-26 04:00 | 5 | 26 | 4 | 2.951% | 30.48%
2024-05-26 05:00 | 5 | 26 | 5 | 6.187% | 28.49%
2024-05-26 06:00 | 5 | 26 | 6 | 19.07% | 26.56%
2024-05-26 07:00 | 5 | 26 | 7 | 40.44% | 25.33%
2024-05-26 08:00 | 5 | 26 | 8 | 58.21% | 25.32%
2024-05-26 09:00 | 5 | 26 | 9 | 72.21% | 26.44%
2024-05-26 10:00 | 5 | 26 | 10 | 75.41% | 27.64%
2024-05-26 11:00 | 5 | 26 | 11 | 75.41% | 29.6%
2024-05-26 12:00 | 5 | 26 | 12 | 75.41% | 31.15%
2024-05-26 13:00 | 5 | 26 | 13 | 75.41% | 31.99%
2024-05-26 14:00 | 5 | 26 | 14 | 74.78% | 32.38%
2024-05-26 15:00 | 5 | 26 | 15 | 61.63% | 32.93%
2024-05-26 16:00 | 5 | 26 | 16 | 43.98% | 32.61%
2024-05-26 17:00 | 5 | 26 | 17 | 24% | 31.12%
2024-05-26 18:00 | 5 | 26 | 18 | 7.246% | 29.43%
2024-05-26 19:00 | 5 | 26 | 19 | 3.556% | 28.66%
2024-05-26 20:00 | 5 | 26 | 20 | 0% | 29.17%
2024-05-26 21:00 | 5 | 26 | 21 | 0% | 30.04%
2024-05-26 22:00 | 5 | 26 | 22 | 0% | 30.57%
2024-05-26 23:00 | 5 | 26 | 23 | 0% | 30.33%
2024-05-27 | 5 | 27 | 0 | 0% | 31.63%
2024-05-27 01:00 | 5 | 27 | 1 | 0% | 28.26%
2024-05-27 02:00 | 5 | 27 | 2 | 0% | 27.09%
2024-05-27 03:00 | 5 | 27 | 3 | 0% | 25.67%
2024-05-27 04:00 | 5 | 27 | 4 | 2.956% | 24.03%
2024-05-27 05:00 | 5 | 27 | 5 | 7.092% | 21.93%
2024-05-27 06:00 | 5 | 27 | 6 | 18.94% | 20.39%
2024-05-27 07:00 | 5 | 27 | 7 | 40.33% | 20.06%
2024-05-27 08:00 | 5 | 27 | 8 | 58.03% | 21.39%
2024-05-27 09:00 | 5 | 27 | 9 | 71.67% | 23.23%
2024-05-27 10:00 | 5 | 27 | 10 | 75.41% | 25.42%
2024-05-27 11:00 | 5 | 27 | 11 | 75.41% | 27.71%
2024-05-27 12:00 | 5 | 27 | 12 | 75.41% | 30.08%
2024-05-27 13:00 | 5 | 27 | 13 | 75.41% | 31.36%
2024-05-27 14:00 | 5 | 27 | 14 | 74.53% | 32.9%
2024-05-27 15:00 | 5 | 27 | 15 | 61.49% | 34.45%
2024-05-27 16:00 | 5 | 27 | 16 | 44.03% | 33.85%
2024-05-27 17:00 | 5 | 27 | 17 | 24.12% | 33.19%
2024-05-27 18:00 | 5 | 27 | 18 | 7.506% | 31.84%
2024-05-27 19:00 | 5 | 27 | 19 | 3.618% | 31.07%
2024-05-27 20:00 | 5 | 27 | 20 | 0% | 33.29%
2024-05-27 21:00 | 5 | 27 | 21 | 0% | 32.43%
2024-05-27 22:00 | 5 | 27 | 22 | 0% | 33.09%
2024-05-27 23:00 | 5 | 27 | 23 | 0% | 32.18%
2024-05-28 | 5 | 28 | 0 | 0% | 28.26%
2024-05-28 01:00 | 5 | 28 | 1 | 0% | 30.84%
2024-05-28 02:00 | 5 | 28 | 2 | 0% | 29.5%
2024-05-28 03:00 | 5 | 28 | 3 | 0% | 28.02%
2024-05-28 04:00 | 5 | 28 | 4 | 3.216% | 25.8%
2024-05-28 05:00 | 5 | 28 | 5 | 6.748% | 22.47%
2024-05-28 06:00 | 5 | 28 | 6 | 18.55% | 19.84%
2024-05-28 07:00 | 5 | 28 | 7 | 40.42% | 18.29%
2024-05-28 08:00 | 5 | 28 | 8 | 53.52% | 17.73%
2024-05-28 09:00 | 5 | 28 | 9 | 20.82% | 18.31%
2024-05-28 10:00 | 5 | 28 | 10 | 16.04% | 18.81%
2024-05-28 11:00 | 5 | 28 | 11 | 12.59% | 19.87%
2024-05-28 12:00 | 5 | 28 | 12 | 31.59% | 20.83%
2024-05-28 13:00 | 5 | 28 | 13 | 75.41% | 20.93%
2024-05-28 14:00 | 5 | 28 | 14 | 74.28% | 21.2%
2024-05-28 15:00 | 5 | 28 | 15 | 55.36% | 21.59%
2024-05-28 16:00 | 5 | 28 | 16 | 18.56% | 21.95%
2024-05-28 17:00 | 5 | 28 | 17 | 12.12% | 21.33%
2024-05-28 18:00 | 5 | 28 | 18 | 8.708% | 20.68%
2024-05-28 19:00 | 5 | 28 | 19 | 2.672% | 21.39%
2024-05-28 20:00 | 5 | 28 | 20 | 0% | 22.77%
2024-05-28 21:00 | 5 | 28 | 21 | 0% | 24.79%
2024-05-28 22:00 | 5 | 28 | 22 | 0% | 25.89%
2024-05-28 23:00 | 5 | 28 | 23 | 0% | 27.39%
2024-05-29 | 5 | 29 | 0 | 0% | 23.67%
2024-05-29 01:00 | 5 | 29 | 1 | 0% | 29.16%
2024-05-29 02:00 | 5 | 29 | 2 | 0% | 25.94%
2024-05-29 03:00 | 5 | 29 | 3 | 0% | 24.67%
2024-05-29 04:00 | 5 | 29 | 4 | 0.3683% | 22.38%
2024-05-29 05:00 | 5 | 29 | 5 | 0.9511% | 19.27%
2024-05-29 06:00 | 5 | 29 | 6 | 3.985% | 16.35%
2024-05-29 07:00 | 5 | 29 | 7 | 7.077% | 14.73%
2024-05-29 08:00 | 5 | 29 | 8 | 10.72% | 13.75%
2024-05-29 09:00 | 5 | 29 | 9 | 16.78% | 13.96%
2024-05-29 10:00 | 5 | 29 | 10 | 17.3% | 14.28%
2024-05-29 11:00 | 5 | 29 | 11 | 15.79% | 12.58%
2024-05-29 12:00 | 5 | 29 | 12 | 17.45% | 16.36%
2024-05-29 13:00 | 5 | 29 | 13 | 15.76% | 16.98%
2024-05-29 14:00 | 5 | 29 | 14 | 14% | 17.1%
2024-05-29 15:00 | 5 | 29 | 15 | 15.79% | 18.6%
2024-05-29 16:00 | 5 | 29 | 16 | 8.814% | 17.38%
2024-05-29 17:00 | 5 | 29 | 17 | 3.244% | 16.64%
2024-05-29 18:00 | 5 | 29 | 18 | 6.324% | 15.97%
2024-05-29 19:00 | 5 | 29 | 19 | 2.47% | 15.86%
2024-05-29 20:00 | 5 | 29 | 20 | 0% | 17.28%
2024-05-29 21:00 | 5 | 29 | 21 | 0% | 20.01%
2024-05-29 22:00 | 5 | 29 | 22 | 0% | 21.82%
2024-05-29 23:00 | 5 | 29 | 23 | 0% | 23.14%
2024-05-30 | 5 | 30 | 0 | 0% | 33.82%
2024-05-30 01:00 | 5 | 30 | 1 | 0% | 23.93%
2024-05-30 02:00 | 5 | 30 | 2 | 0% | 24.03%
2024-05-30 03:00 | 5 | 30 | 3 | 0% | 23.78%
2024-05-30 04:00 | 5 | 30 | 4 | 0% | 23.2%
2024-05-30 05:00 | 5 | 30 | 5 | 1.314% | 22.11%
2024-05-30 06:00 | 5 | 30 | 6 | 3.444% | 20.6%
2024-05-30 07:00 | 5 | 30 | 7 | 5.932% | 20.08%
2024-05-30 08:00 | 5 | 30 | 8 | 14.3% | 20.98%
2024-05-30 09:00 | 5 | 30 | 9 | 14.05% | 24.55%
2024-05-30 10:00 | 5 | 30 | 10 | 12.63% | 23.37%
2024-05-30 11:00 | 5 | 30 | 11 | 11.11% | 24.38%
2024-05-30 12:00 | 5 | 30 | 12 | 13.11% | 25.69%
2024-05-30 13:00 | 5 | 30 | 13 | 13.38% | 25.45%
2024-05-30 14:00 | 5 | 30 | 14 | 10.54% | 26.55%
2024-05-30 15:00 | 5 | 30 | 15 | 14.97% | 28.19%
2024-05-30 16:00 | 5 | 30 | 16 | 15.41% | 28.81%
2024-05-30 17:00 | 5 | 30 | 17 | 12.04% | 28.7%
2024-05-30 18:00 | 5 | 30 | 18 | 7.408% | 28.65%
2024-05-30 19:00 | 5 | 30 | 19 | 3.764% | 29.64%
2024-05-30 20:00 | 5 | 30 | 20 | 0.2426% | 31.8%
2024-05-30 21:00 | 5 | 30 | 21 | 0% | 33.4%
2024-05-30 22:00 | 5 | 30 | 22 | 0% | 33.73%
2024-05-30 23:00 | 5 | 30 | 23 | 0% | 35.07%
2024-05-31 | 5 | 31 | 0 | 0% | 21.1%
2024-05-31 01:00 | 5 | 31 | 1 | 0% | 33.46%
2024-05-31 02:00 | 5 | 31 | 2 | 0% | 32.46%
2024-05-31 03:00 | 5 | 31 | 3 | 0% | 31.97%
2024-05-31 04:00 | 5 | 31 | 4 | 0.4603% | 30.07%
2024-05-31 05:00 | 5 | 31 | 5 | 2.75% | 26.68%
2024-05-31 06:00 | 5 | 31 | 6 | 4.842% | 23.12%
2024-05-31 07:00 | 5 | 31 | 7 | 8.061% | 20.44%
2024-05-31 08:00 | 5 | 31 | 8 | 11.56% | 19.74%
2024-05-31 09:00 | 5 | 31 | 9 | 16.14% | 19.36%
2024-05-31 10:00 | 5 | 31 | 10 | 15.88% | 19.58%
2024-05-31 11:00 | 5 | 31 | 11 | 25.47% | 20.25%
2024-05-31 12:00 | 5 | 31 | 12 | 28.79% | 20.6%
2024-05-31 13:00 | 5 | 31 | 13 | 31.64% | 21.05%
2024-05-31 14:00 | 5 | 31 | 14 | 47.72% | 21.2%
2024-05-31 15:00 | 5 | 31 | 15 | 37.36% | 21.12%
2024-05-31 16:00 | 5 | 31 | 16 | 25.52% | 20.81%
2024-05-31 17:00 | 5 | 31 | 17 | 15.54% | 19.48%
2024-05-31 18:00 | 5 | 31 | 18 | 8.404% | 19.15%
2024-05-31 19:00 | 5 | 31 | 19 | 3.612% | 16.63%
2024-05-31 20:00 | 5 | 31 | 20 | 0.5827% | 16.88%
2024-05-31 21:00 | 5 | 31 | 21 | 0% | 18.7%
2024-05-31 22:00 | 5 | 31 | 22 | 0% | 19.97%
2024-05-31 23:00 | 5 | 31 | 23 | 0% | 20.67%
2024-06-01 | 6 | 1 | 0 | 0% | 26.26%
2024-06-01 01:00 | 6 | 1 | 1 | 0% | 21.57%
2024-06-01 02:00 | 6 | 1 | 2 | 0% | 21.69%
2024-06-01 03:00 | 6 | 1 | 3 | 0% | 21.63%
2024-06-01 04:00 | 6 | 1 | 4 | 2.46% | 20.51%
2024-06-01 05:00 | 6 | 1 | 5 | 4.72% | 19%
2024-06-01 06:00 | 6 | 1 | 6 | 7.101% | 17.96%
2024-06-01 07:00 | 6 | 1 | 7 | 9.233% | 17.81%
2024-06-01 08:00 | 6 | 1 | 8 | 20.1% | 18.72%
2024-06-01 09:00 | 6 | 1 | 9 | 22.21% | 20.56%
2024-06-01 10:00 | 6 | 1 | 10 | 26.11% | 22.84%
2024-06-01 11:00 | 6 | 1 | 11 | 38.3% | 24.1%
2024-06-01 12:00 | 6 | 1 | 12 | 75.41% | 27.55%
2024-06-01 13:00 | 6 | 1 | 13 | 75.41% | 26.05%
2024-06-01 14:00 | 6 | 1 | 14 | 63.73% | 26.51%
2024-06-01 15:00 | 6 | 1 | 15 | 48.22% | 26.43%
2024-06-01 16:00 | 6 | 1 | 16 | 39% | 26.31%
2024-06-01 17:00 | 6 | 1 | 17 | 25.4% | 25.78%
2024-06-01 18:00 | 6 | 1 | 18 | 7.498% | 24.34%
2024-06-01 19:00 | 6 | 1 | 19 | 3.817% | 23.9%
2024-06-01 20:00 | 6 | 1 | 20 | 0.8566% | 24.16%
2024-06-01 21:00 | 6 | 1 | 21 | 0% | 25.02%
2024-06-01 22:00 | 6 | 1 | 22 | 0% | 25.2%
2024-06-01 23:00 | 6 | 1 | 23 | 0% | 27.4%
2024-06-02 | 6 | 2 | 0 | 0% | 23.43%
2024-06-02 01:00 | 6 | 2 | 1 | 0% | 26.67%
2024-06-02 02:00 | 6 | 2 | 2 | 0% | 26.94%
2024-06-02 03:00 | 6 | 2 | 3 | 0% | 26.67%
2024-06-02 04:00 | 6 | 2 | 4 | 3.171% | 25.05%
2024-06-02 05:00 | 6 | 2 | 5 | 5.965% | 22.21%
2024-06-02 06:00 | 6 | 2 | 6 | 17.84% | 20.02%
2024-06-02 07:00 | 6 | 2 | 7 | 20.29% | 18.87%
2024-06-02 08:00 | 6 | 2 | 8 | 17.71% | 18.98%
2024-06-02 09:00 | 6 | 2 | 9 | 34.87% | 19.87%
2024-06-02 10:00 | 6 | 2 | 10 | 22.16% | 20.68%
2024-06-02 11:00 | 6 | 2 | 11 | 21.58% | 21.33%
2024-06-02 12:00 | 6 | 2 | 12 | 16.46% | 21.91%
2024-06-02 13:00 | 6 | 2 | 13 | 29.54% | 22.2%
2024-06-02 14:00 | 6 | 2 | 14 | 19.79% | 21.99%
2024-06-02 15:00 | 6 | 2 | 15 | 17.72% | 21.51%
2024-06-02 16:00 | 6 | 2 | 16 | 13.82% | 21.22%
2024-06-02 17:00 | 6 | 2 | 17 | 16.44% | 21.42%
2024-06-02 18:00 | 6 | 2 | 18 | 8.099% | 18.38%
2024-06-02 19:00 | 6 | 2 | 19 | 3.595% | 17.8%
2024-06-02 20:00 | 6 | 2 | 20 | 0.32% | 19.26%
2024-06-02 21:00 | 6 | 2 | 21 | 0% | 21.48%
2024-06-02 22:00 | 6 | 2 | 22 | 0% | 22.67%
2024-06-02 23:00 | 6 | 2 | 23 | 0% | 23.2%
2024-06-03 | 6 | 3 | 0 | 0% | 36.11%
2024-06-03 01:00 | 6 | 3 | 1 | 0% | 23.54%
2024-06-03 02:00 | 6 | 3 | 2 | 0% | 24.08%
2024-06-03 03:00 | 6 | 3 | 3 | 0% | 24.01%
2024-06-03 04:00 | 6 | 3 | 4 | 3.429% | 22.61%
2024-06-03 05:00 | 6 | 3 | 5 | 7.172% | 16.78%
2024-06-03 06:00 | 6 | 3 | 6 | 16.31% | 17.82%
2024-06-03 07:00 | 6 | 3 | 7 | 40.81% | 16.57%
2024-06-03 08:00 | 6 | 3 | 8 | 58.4% | 16.69%
2024-06-03 09:00 | 6 | 3 | 9 | 72.23% | 17.31%
2024-06-03 10:00 | 6 | 3 | 10 | 70.7% | 18.52%
2024-06-03 11:00 | 6 | 3 | 11 | 75.41% | 19.78%
2024-06-03 12:00 | 6 | 3 | 12 | 75.41% | 21.38%
2024-06-03 13:00 | 6 | 3 | 13 | 74.13% | 23%
2024-06-03 14:00 | 6 | 3 | 14 | 74.66% | 23.43%
2024-06-03 15:00 | 6 | 3 | 15 | 49.6% | 25.91%
2024-06-03 16:00 | 6 | 3 | 16 | 39.01% | 26.93%
2024-06-03 17:00 | 6 | 3 | 17 | 24.79% | 26.9%
2024-06-03 18:00 | 6 | 3 | 18 | 8.199% | 27.51%
2024-06-03 19:00 | 6 | 3 | 19 | 3.657% | 28.51%
2024-06-03 20:00 | 6 | 3 | 20 | 1.478% | 30.76%
2024-06-03 21:00 | 6 | 3 | 21 | 0% | 33.39%
2024-06-03 22:00 | 6 | 3 | 22 | 0% | 35.32%
2024-06-03 23:00 | 6 | 3 | 23 | 0% | 36.33%
2024-06-04 | 6 | 4 | 0 | 0% | 27.41%
2024-06-04 01:00 | 6 | 4 | 1 | 0% | 35.4%
2024-06-04 02:00 | 6 | 4 | 2 | 0% | 33.9%
2024-06-04 03:00 | 6 | 4 | 3 | 0% | 32.32%
2024-06-04 04:00 | 6 | 4 | 4 | 4.185% | 29.73%
2024-06-04 05:00 | 6 | 4 | 5 | 5.895% | 26.29%
2024-06-04 06:00 | 6 | 4 | 6 | 21.57% | 23.11%
2024-06-04 07:00 | 6 | 4 | 7 | 41.6% | 20.39%
2024-06-04 08:00 | 6 | 4 | 8 | 59.13% | 19.18%
2024-06-04 09:00 | 6 | 4 | 9 | 72.77% | 19.34%
2024-06-04 10:00 | 6 | 4 | 10 | 75.41% | 20.1%
2024-06-04 11:00 | 6 | 4 | 11 | 75.41% | 20.93%
2024-06-04 12:00 | 6 | 4 | 12 | 75.41% | 21.16%
2024-06-04 13:00 | 6 | 4 | 13 | 75.41% | 21.33%
2024-06-04 14:00 | 6 | 4 | 14 | 74.69% | 21.68%
2024-06-04 15:00 | 6 | 4 | 15 | 61.42% | 21.29%
2024-06-04 16:00 | 6 | 4 | 16 | 44.1% | 20.99%
2024-06-04 17:00 | 6 | 4 | 17 | 24.82% | 21.53%
2024-06-04 18:00 | 6 | 4 | 18 | 8.244% | 18.98%
2024-06-04 19:00 | 6 | 4 | 19 | 4.396% | 18.7%
2024-06-04 20:00 | 6 | 4 | 20 | 0.6633% | 20%
2024-06-04 21:00 | 6 | 4 | 21 | 0% | 22.26%
2024-06-04 22:00 | 6 | 4 | 22 | 0% | 24.06%
2024-06-04 23:00 | 6 | 4 | 23 | 0% | 26.01%
2024-06-05 | 6 | 5 | 0 | 0% | 23.81%
2024-06-05 01:00 | 6 | 5 | 1 | 0% | 28.37%
2024-06-05 02:00 | 6 | 5 | 2 | 0% | 28.82%
2024-06-05 03:00 | 6 | 5 | 3 | 0% | 28.7%
2024-06-05 04:00 | 6 | 5 | 4 | 4.188% | 28.22%
2024-06-05 05:00 | 6 | 5 | 5 | 6.461% | 26.92%
2024-06-05 06:00 | 6 | 5 | 6 | 21.33% | 25.8%
2024-06-05 07:00 | 6 | 5 | 7 | 41.02% | 25.38%
2024-06-05 08:00 | 6 | 5 | 8 | 58.41% | 25.88%
2024-06-05 09:00 | 6 | 5 | 9 | 72.3% | 26.95%
2024-06-05 10:00 | 6 | 5 | 10 | 75.41% | 28.37%
2024-06-05 11:00 | 6 | 5 | 11 | 75.41% | 29.15%
2024-06-05 12:00 | 6 | 5 | 12 | 75.41% | 29.51%
2024-06-05 13:00 | 6 | 5 | 13 | 75.41% | 29.4%
2024-06-05 14:00 | 6 | 5 | 14 | 75.12% | 30.64%
2024-06-05 15:00 | 6 | 5 | 15 | 62.28% | 27.64%
2024-06-05 16:00 | 6 | 5 | 16 | 45.07% | 25.45%
2024-06-05 17:00 | 6 | 5 | 17 | 21.57% | 23.22%
2024-06-05 18:00 | 6 | 5 | 18 | 6.696% | 20.92%
2024-06-05 19:00 | 6 | 5 | 19 | 4.002% | 19.33%
2024-06-05 20:00 | 6 | 5 | 20 | 0% | 19.42%
2024-06-05 21:00 | 6 | 5 | 21 | 0% | 20.33%
2024-06-05 22:00 | 6 | 5 | 22 | 0% | 21.89%
2024-06-05 23:00 | 6 | 5 | 23 | 0% | 23.28%
2024-06-06 | 6 | 6 | 0 | 0% | 37.13%
2024-06-06 01:00 | 6 | 6 | 1 | 0% | 23.79%
2024-06-06 02:00 | 6 | 6 | 2 | 0% | 23.57%
2024-06-06 03:00 | 6 | 6 | 3 | 0% | 22.82%
2024-06-06 04:00 | 6 | 6 | 4 | 3.537% | 21.62%
2024-06-06 05:00 | 6 | 6 | 5 | 6.165% | 19.41%
2024-06-06 06:00 | 6 | 6 | 6 | 17.52% | 17.09%
2024-06-06 07:00 | 6 | 6 | 7 | 40.37% | 16.05%
2024-06-06 08:00 | 6 | 6 | 8 | 57.82% | 16.34%
2024-06-06 09:00 | 6 | 6 | 9 | 71.32% | 17.26%
2024-06-06 10:00 | 6 | 6 | 10 | 75.41% | 18.14%
2024-06-06 11:00 | 6 | 6 | 11 | 75.41% | 19.27%
2024-06-06 12:00 | 6 | 6 | 12 | 75.41% | 20.77%
2024-06-06 13:00 | 6 | 6 | 13 | 75.41% | 22.58%
2024-06-06 14:00 | 6 | 6 | 14 | 74.95% | 24.71%
2024-06-06 15:00 | 6 | 6 | 15 | 62.58% | 26.74%
2024-06-06 16:00 | 6 | 6 | 16 | 45.22% | 28.09%
2024-06-06 17:00 | 6 | 6 | 17 | 25.7% | 29.13%
2024-06-06 18:00 | 6 | 6 | 18 | 8.82% | 29.88%
2024-06-06 19:00 | 6 | 6 | 19 | 3.916% | 31.23%
2024-06-06 20:00 | 6 | 6 | 20 | 1.159% | 33.31%
2024-06-06 21:00 | 6 | 6 | 21 | 0% | 35.03%
2024-06-06 22:00 | 6 | 6 | 22 | 0% | 36.38%
2024-06-06 23:00 | 6 | 6 | 23 | 0% | 35.99%
2024-06-07 | 6 | 7 | 0 | 0% | 21.75%
2024-06-07 01:00 | 6 | 7 | 1 | 0% | 36.51%
2024-06-07 02:00 | 6 | 7 | 2 | 0% | 36.32%
2024-06-07 03:00 | 6 | 7 | 3 | 0% | 35.48%
2024-06-07 04:00 | 6 | 7 | 4 | 2.531% | 34.28%
2024-06-07 05:00 | 6 | 7 | 5 | 4.391% | 32.1%
2024-06-07 06:00 | 6 | 7 | 6 | 7.291% | 30.62%
2024-06-07 07:00 | 6 | 7 | 7 | 6.561% | 29.85%
2024-06-07 08:00 | 6 | 7 | 8 | 10.49% | 29.7%
2024-06-07 09:00 | 6 | 7 | 9 | 10.78% | 29.71%
2024-06-07 10:00 | 6 | 7 | 10 | 14.94% | 30.18%
2024-06-07 11:00 | 6 | 7 | 11 | 23.45% | 30.06%
2024-06-07 12:00 | 6 | 7 | 12 | 13.95% | 30.26%
2024-06-07 13:00 | 6 | 7 | 13 | 17.23% | 30%
2024-06-07 14:00 | 6 | 7 | 14 | 11.05% | 29.24%
2024-06-07 15:00 | 6 | 7 | 15 | 18.8% | 28.68%
2024-06-07 16:00 | 6 | 7 | 16 | 18.56% | 28.05%
2024-06-07 17:00 | 6 | 7 | 17 | 19.75% | 27.01%
2024-06-07 18:00 | 6 | 7 | 18 | 9.575% | 23.36%
2024-06-07 19:00 | 6 | 7 | 19 | 4.146% | 22.15%
2024-06-07 20:00 | 6 | 7 | 20 | 1.935% | 22.29%
2024-06-07 21:00 | 6 | 7 | 21 | 0% | 23.17%
2024-06-07 22:00 | 6 | 7 | 22 | 0% | 24.88%
2024-06-07 23:00 | 6 | 7 | 23 | 0% | 24.57%
2024-06-08 | 6 | 8 | 0 | 0% | 25.38%
2024-06-08 01:00 | 6 | 8 | 1 | 0% | 20.3%
2024-06-08 02:00 | 6 | 8 | 2 | 0% | 18.82%
2024-06-08 03:00 | 6 | 8 | 3 | 0% | 17.5%
2024-06-08 04:00 | 6 | 8 | 4 | 3.219% | 15.57%
2024-06-08 05:00 | 6 | 8 | 5 | 6.71% | 13.9%
2024-06-08 06:00 | 6 | 8 | 6 | 7.447% | 12.9%
2024-06-08 07:00 | 6 | 8 | 7 | 9.347% | 12.52%
2024-06-08 08:00 | 6 | 8 | 8 | 15.13% | 12.73%
2024-06-08 09:00 | 6 | 8 | 9 | 19.94% | 12.95%
2024-06-08 10:00 | 6 | 8 | 10 | 16.45% | 13.42%
2024-06-08 11:00 | 6 | 8 | 11 | 20.14% | 15.05%
2024-06-08 12:00 | 6 | 8 | 12 | 36.42% | 15.74%
2024-06-08 13:00 | 6 | 8 | 13 | 56.76% | 15.32%
2024-06-08 14:00 | 6 | 8 | 14 | 66.55% | 16.03%
2024-06-08 15:00 | 6 | 8 | 15 | 54.01% | 16.52%
2024-06-08 16:00 | 6 | 8 | 16 | 46.09% | 17.89%
2024-06-08 17:00 | 6 | 8 | 17 | 26.29% | 17.81%
2024-06-08 18:00 | 6 | 8 | 18 | 9.176% | 17.9%
2024-06-08 19:00 | 6 | 8 | 19 | 4.129% | 18.16%
2024-06-08 20:00 | 6 | 8 | 20 | 1.404% | 19.28%
2024-06-08 21:00 | 6 | 8 | 21 | 0% | 20.71%
2024-06-08 22:00 | 6 | 8 | 22 | 0% | 22.26%
2024-06-08 23:00 | 6 | 8 | 23 | 0% | 22.99%
2024-06-09 | 6 | 9 | 0 | 0% | 28.32%
2024-06-09 01:00 | 6 | 9 | 1 | 0% | 23.77%
2024-06-09 02:00 | 6 | 9 | 2 | 0% | 23.53%
2024-06-09 03:00 | 6 | 9 | 3 | 0% | 23.09%
2024-06-09 04:00 | 6 | 9 | 4 | 2.452% | 21.95%
2024-06-09 05:00 | 6 | 9 | 5 | 5.393% | 20.64%
2024-06-09 06:00 | 6 | 9 | 6 | 11.13% | 19.6%
2024-06-09 07:00 | 6 | 9 | 7 | 30.65% | 18.86%
2024-06-09 08:00 | 6 | 9 | 8 | 58.64% | 18.72%
2024-06-09 09:00 | 6 | 9 | 9 | 72.77% | 18.95%
2024-06-09 10:00 | 6 | 9 | 10 | 75.41% | 20%
2024-06-09 11:00 | 6 | 9 | 11 | 75.41% | 20.85%
2024-06-09 12:00 | 6 | 9 | 12 | 75.41% | 20.66%
2024-06-09 13:00 | 6 | 9 | 13 | 75.41% | 21.57%
2024-06-09 14:00 | 6 | 9 | 14 | 75.41% | 22.37%
2024-06-09 15:00 | 6 | 9 | 15 | 48.87% | 24.1%
2024-06-09 16:00 | 6 | 9 | 16 | 39.67% | 24.77%
2024-06-09 17:00 | 6 | 9 | 17 | 26.6% | 24.4%
2024-06-09 18:00 | 6 | 9 | 18 | 9.038% | 24.26%
2024-06-09 19:00 | 6 | 9 | 19 | 3.884% | 23.98%
2024-06-09 20:00 | 6 | 9 | 20 | 2.329% | 25.6%
2024-06-09 21:00 | 6 | 9 | 21 | 0% | 27.6%
2024-06-09 22:00 | 6 | 9 | 22 | 0% | 28.13%
2024-06-09 23:00 | 6 | 9 | 23 | 0% | 28.18%
2024-06-10 | 6 | 10 | 0 | 0% | 24.16%
2024-06-10 01:00 | 6 | 10 | 1 | 0% | 27.99%
2024-06-10 02:00 | 6 | 10 | 2 | 0% | 26.86%
2024-06-10 03:00 | 6 | 10 | 3 | 0% | 25.29%
2024-06-10 04:00 | 6 | 10 | 4 | 3.718% | 23.06%
2024-06-10 05:00 | 6 | 10 | 5 | 6.094% | 20.53%
2024-06-10 06:00 | 6 | 10 | 6 | 17.77% | 18.24%
2024-06-10 07:00 | 6 | 10 | 7 | 25.8% | 17.42%
2024-06-10 08:00 | 6 | 10 | 8 | 45.46% | 17.38%
2024-06-10 09:00 | 6 | 10 | 9 | 60.1% | 17.41%
2024-06-10 10:00 | 6 | 10 | 10 | 75.41% | 17.55%
2024-06-10 11:00 | 6 | 10 | 11 | 62.63% | 18.37%
2024-06-10 12:00 | 6 | 10 | 12 | 53.87% | 18.97%
2024-06-10 13:00 | 6 | 10 | 13 | 63.06% | 19.92%
2024-06-10 14:00 | 6 | 10 | 14 | 43.53% | 20.32%
2024-06-10 15:00 | 6 | 10 | 15 | 47.53% | 20.42%
2024-06-10 16:00 | 6 | 10 | 16 | 36.93% | 20.34%
2024-06-10 17:00 | 6 | 10 | 17 | 23.11% | 19.11%
2024-06-10 18:00 | 6 | 10 | 18 | 8.886% | 18.18%
2024-06-10 19:00 | 6 | 10 | 19 | 3.872% | 17.27%
2024-06-10 20:00 | 6 | 10 | 20 | 1.164% | 18.73%
2024-06-10 21:00 | 6 | 10 | 21 | 0% | 21.71%
2024-06-10 22:00 | 6 | 10 | 22 | 0% | 23.21%
2024-06-10 23:00 | 6 | 10 | 23 | 0% | 24.06%
2024-06-11 | 6 | 11 | 0 | 0% | 34.85%
2024-06-11 01:00 | 6 | 11 | 1 | 0% | 23.65%
2024-06-11 02:00 | 6 | 11 | 2 | 0% | 24.47%
2024-06-11 03:00 | 6 | 11 | 3 | 0% | 22.65%
2024-06-11 04:00 | 6 | 11 | 4 | 3.181% | 20.96%
2024-06-11 05:00 | 6 | 11 | 5 | 5.725% | 18.08%
2024-06-11 06:00 | 6 | 11 | 6 | 7.515% | 16.11%
2024-06-11 07:00 | 6 | 11 | 7 | 12.17% | 16.12%
2024-06-11 08:00 | 6 | 11 | 8 | 23.06% | 17.54%
2024-06-11 09:00 | 6 | 11 | 9 | 19.5% | 19.57%
2024-06-11 10:00 | 6 | 11 | 10 | 18.8% | 21.91%
2024-06-11 11:00 | 6 | 11 | 11 | 19.08% | 24.25%
2024-06-11 12:00 | 6 | 11 | 12 | 36.45% | 26.03%
2024-06-11 13:00 | 6 | 11 | 13 | 57.77% | 29.64%
2024-06-11 14:00 | 6 | 11 | 14 | 61.56% | 29.4%
2024-06-11 15:00 | 6 | 11 | 15 | 39.75% | 30.79%
2024-06-11 16:00 | 6 | 11 | 16 | 37.63% | 31.55%
2024-06-11 17:00 | 6 | 11 | 17 | 16.03% | 30.63%
2024-06-11 18:00 | 6 | 11 | 18 | 7.212% | 27.54%
2024-06-11 19:00 | 6 | 11 | 19 | 2.533% | 30.5%
2024-06-11 20:00 | 6 | 11 | 20 | 0.3184% | 29.54%
2024-06-11 21:00 | 6 | 11 | 21 | 0% | 31.39%
2024-06-11 22:00 | 6 | 11 | 22 | 0% | 32.9%
2024-06-11 23:00 | 6 | 11 | 23 | 0% | 34.3%
2024-06-12 | 6 | 12 | 0 | 0% | 30.1%
2024-06-12 01:00 | 6 | 12 | 1 | 0% | 34.81%
2024-06-12 02:00 | 6 | 12 | 2 | 0% | 34.56%
2024-06-12 03:00 | 6 | 12 | 3 | 0% | 34.17%
2024-06-12 04:00 | 6 | 12 | 4 | 3.601% | 32.95%
2024-06-12 05:00 | 6 | 12 | 5 | 8.194% | 30.57%
2024-06-12 06:00 | 6 | 12 | 6 | 16.81% | 27.98%
2024-06-12 07:00 | 6 | 12 | 7 | 30.93% | 26.28%
2024-06-12 08:00 | 6 | 12 | 8 | 40.5% | 26.25%
2024-06-12 09:00 | 6 | 12 | 9 | 35.99% | 27.12%
2024-06-12 10:00 | 6 | 12 | 10 | 59.9% | 27.96%
2024-06-12 11:00 | 6 | 12 | 11 | 75.41% | 28.96%
2024-06-12 12:00 | 6 | 12 | 12 | 75.41% | 29.64%
2024-06-12 13:00 | 6 | 12 | 13 | 75.41% | 30.05%
2024-06-12 14:00 | 6 | 12 | 14 | 75.41% | 30.01%
2024-06-12 15:00 | 6 | 12 | 15 | 65.1% | 30.08%
2024-06-12 16:00 | 6 | 12 | 16 | 47.45% | 29.57%
2024-06-12 17:00 | 6 | 12 | 17 | 27.52% | 28.77%
2024-06-12 18:00 | 6 | 12 | 18 | 9.759% | 30%
2024-06-12 19:00 | 6 | 12 | 19 | 4.289% | 26.71%
2024-06-12 20:00 | 6 | 12 | 20 | 2.368% | 27.45%
2024-06-12 21:00 | 6 | 12 | 21 | 0% | 28.87%
2024-06-12 22:00 | 6 | 12 | 22 | 0% | 30.1%
2024-06-12 23:00 | 6 | 12 | 23 | 0% | 30.48%
2024-06-13 | 6 | 13 | 0 | 0% | 19.95%
2024-06-13 01:00 | 6 | 13 | 1 | 0% | 29.53%
2024-06-13 02:00 | 6 | 13 | 2 | 0% | 28.28%
2024-06-13 03:00 | 6 | 13 | 3 | 0% | 26.79%
2024-06-13 04:00 | 6 | 13 | 4 | 4.474% | 24.03%
2024-06-13 05:00 | 6 | 13 | 5 | 6.289% | 20.89%
2024-06-13 06:00 | 6 | 13 | 6 | 22.11% | 18.18%
2024-06-13 07:00 | 6 | 13 | 7 | 42.48% | 16.65%
2024-06-13 08:00 | 6 | 13 | 8 | 60.46% | 16.03%
2024-06-13 09:00 | 6 | 13 | 9 | 74.82% | 16.27%
2024-06-13 10:00 | 6 | 13 | 10 | 75.41% | 16.43%
2024-06-13 11:00 | 6 | 13 | 11 | 75.41% | 16.66%
2024-06-13 12:00 | 6 | 13 | 12 | 75.41% | 16.75%
2024-06-13 13:00 | 6 | 13 | 13 | 75.41% | 17.96%
2024-06-13 14:00 | 6 | 13 | 14 | 75.41% | 16.62%
2024-06-13 15:00 | 6 | 13 | 15 | 58.47% | 17.42%
2024-06-13 16:00 | 6 | 13 | 16 | 46.92% | 15.61%
2024-06-13 17:00 | 6 | 13 | 17 | 27.01% | 14.87%
2024-06-13 18:00 | 6 | 13 | 18 | 9.493% | 13.87%
2024-06-13 19:00 | 6 | 13 | 19 | 4.054% | 14.74%
2024-06-13 20:00 | 6 | 13 | 20 | 2.515% | 14.69%
2024-06-13 21:00 | 6 | 13 | 21 | 0% | 16.84%
2024-06-13 22:00 | 6 | 13 | 22 | 0% | 17.99%
2024-06-13 23:00 | 6 | 13 | 23 | 0% | 19.03%
2024-06-14 | 6 | 14 | 0 | 0% | 27.16%
2024-06-14 01:00 | 6 | 14 | 1 | 0% | 20.31%
2024-06-14 02:00 | 6 | 14 | 2 | 0% | 20.26%
2024-06-14 03:00 | 6 | 14 | 3 | 0% | 19.61%
2024-06-14 04:00 | 6 | 14 | 4 | 2.862% | 17.94%
2024-06-14 05:00 | 6 | 14 | 5 | 5.166% | 15.48%
2024-06-14 06:00 | 6 | 14 | 6 | 7.901% | 13.31%
2024-06-14 07:00 | 6 | 14 | 7 | 11.92% | 12.22%
2024-06-14 08:00 | 6 | 14 | 8 | 18.49% | 12.26%
2024-06-14 09:00 | 6 | 14 | 9 | 25.87% | 13.27%
2024-06-14 10:00 | 6 | 14 | 10 | 42.93% | 14.8%
2024-06-14 11:00 | 6 | 14 | 11 | 56.42% | 16.01%
2024-06-14 12:00 | 6 | 14 | 12 | 54.13% | 17.37%
2024-06-14 13:00 | 6 | 14 | 13 | 50.48% | 18.9%
2024-06-14 14:00 | 6 | 14 | 14 | 25.81% | 20.15%
2024-06-14 15:00 | 6 | 14 | 15 | 9.585% | 21.03%
2024-06-14 16:00 | 6 | 14 | 16 | 5.867% | 22.14%
2024-06-14 17:00 | 6 | 14 | 17 | 3.674% | 22.32%
2024-06-14 18:00 | 6 | 14 | 18 | 6.505% | 22.4%
2024-06-14 19:00 | 6 | 14 | 19 | 4.183% | 23.21%
2024-06-14 20:00 | 6 | 14 | 20 | 0.418% | 24.6%
2024-06-14 21:00 | 6 | 14 | 21 | 0% | 26.29%
2024-06-14 22:00 | 6 | 14 | 22 | 0% | 27.44%
2024-06-14 23:00 | 6 | 14 | 23 | 0% | 27.75%
2024-06-15 | 6 | 15 | 0 | 0% | 17.24%
2024-06-15 01:00 | 6 | 15 | 1 | 0% | 26.15%
2024-06-15 02:00 | 6 | 15 | 2 | 0% | 25.24%
2024-06-15 03:00 | 6 | 15 | 3 | 0% | 23.98%
2024-06-15 04:00 | 6 | 15 | 4 | 3.856% | 21.75%
2024-06-15 05:00 | 6 | 15 | 5 | 7.074% | 18.87%
2024-06-15 06:00 | 6 | 15 | 6 | 17.76% | 16.84%
2024-06-15 07:00 | 6 | 15 | 7 | 42.18% | 15.46%
2024-06-15 08:00 | 6 | 15 | 8 | 60.13% | 15.44%
2024-06-15 09:00 | 6 | 15 | 9 | 61.58% | 17.31%
2024-06-15 10:00 | 6 | 15 | 10 | 52.68% | 16.98%
2024-06-15 11:00 | 6 | 15 | 11 | 71.56% | 18.16%
2024-06-15 12:00 | 6 | 15 | 12 | 75.41% | 19%
2024-06-15 13:00 | 6 | 15 | 13 | 75.41% | 17.7%
2024-06-15 14:00 | 6 | 15 | 14 | 69.45% | 20.66%
2024-06-15 15:00 | 6 | 15 | 15 | 54.68% | 20.92%
2024-06-15 16:00 | 6 | 15 | 16 | 35.44% | 20.85%
2024-06-15 17:00 | 6 | 15 | 17 | 20.56% | 20.61%
2024-06-15 18:00 | 6 | 15 | 18 | 10.09% | 19.61%
2024-06-15 19:00 | 6 | 15 | 19 | 4.424% | 19.24%
2024-06-15 20:00 | 6 | 15 | 20 | 2.729% | 18.84%
2024-06-15 21:00 | 6 | 15 | 21 | 0% | 19.11%
2024-06-15 22:00 | 6 | 15 | 22 | 0% | 19.23%
2024-06-15 23:00 | 6 | 15 | 23 | 0% | 18.72%
2024-06-16 | 6 | 16 | 0 | 0% | 19.84%
2024-06-16 01:00 | 6 | 16 | 1 | 0% | 17.38%
2024-06-16 02:00 | 6 | 16 | 2 | 0% | 17.45%
2024-06-16 03:00 | 6 | 16 | 3 | 0% | 17.07%
2024-06-16 04:00 | 6 | 16 | 4 | 4.049% | 16.04%
2024-06-16 05:00 | 6 | 16 | 5 | 7.702% | 14.41%
2024-06-16 06:00 | 6 | 16 | 6 | 18.23% | 12.87%
2024-06-16 07:00 | 6 | 16 | 7 | 33.99% | 12.01%
2024-06-16 08:00 | 6 | 16 | 8 | 59.97% | 12.33%
2024-06-16 09:00 | 6 | 16 | 9 | 74.03% | 13.02%
2024-06-16 10:00 | 6 | 16 | 10 | 75.41% | 14.24%
2024-06-16 11:00 | 6 | 16 | 11 | 75.41% | 15.32%
2024-06-16 12:00 | 6 | 16 | 12 | 75.41% | 16.5%
2024-06-16 13:00 | 6 | 16 | 13 | 75.41% | 17.54%
2024-06-16 14:00 | 6 | 16 | 14 | 75.41% | 18.19%
2024-06-16 15:00 | 6 | 16 | 15 | 64.58% | 18.14%
2024-06-16 16:00 | 6 | 16 | 16 | 47.01% | 18.19%
2024-06-16 17:00 | 6 | 16 | 17 | 27.12% | 17.78%
2024-06-16 18:00 | 6 | 16 | 18 | 8.787% | 16.66%
2024-06-16 19:00 | 6 | 16 | 19 | 4.954% | 16.51%
2024-06-16 20:00 | 6 | 16 | 20 | 0.9217% | 17.07%
2024-06-16 21:00 | 6 | 16 | 21 | 0% | 18.06%
2024-06-16 22:00 | 6 | 16 | 22 | 0% | 19.52%
2024-06-16 23:00 | 6 | 16 | 23 | 0% | 19.88%
2024-06-17 | 6 | 17 | 0 | 0% | 32.42%
2024-06-17 01:00 | 6 | 17 | 1 | 0% | 19.48%
2024-06-17 02:00 | 6 | 17 | 2 | 0% | 19.07%
2024-06-17 03:00 | 6 | 17 | 3 | 0% | 18.22%
2024-06-17 04:00 | 6 | 17 | 4 | 3.975% | 16.85%
2024-06-17 05:00 | 6 | 17 | 5 | 6.707% | 14.7%
2024-06-17 06:00 | 6 | 17 | 6 | 17.07% | 12.75%
2024-06-17 07:00 | 6 | 17 | 7 | 35.24% | 11.85%
2024-06-17 08:00 | 6 | 17 | 8 | 48.03% | 12.34%
2024-06-17 09:00 | 6 | 17 | 9 | 69.73% | 13.76%
2024-06-17 10:00 | 6 | 17 | 10 | 75.41% | 15.29%
2024-06-17 11:00 | 6 | 17 | 11 | 75.41% | 17.26%
2024-06-17 12:00 | 6 | 17 | 12 | 75.41% | 18.7%
2024-06-17 13:00 | 6 | 17 | 13 | 75.41% | 21%
2024-06-17 14:00 | 6 | 17 | 14 | 72.34% | 22.79%
2024-06-17 15:00 | 6 | 17 | 15 | 60.33% | 24.48%
2024-06-17 16:00 | 6 | 17 | 16 | 38.65% | 25.49%
2024-06-17 17:00 | 6 | 17 | 17 | 23.25% | 25.35%
2024-06-17 18:00 | 6 | 17 | 18 | 9.876% | 25.04%
2024-06-17 19:00 | 6 | 17 | 19 | 4.083% | 25.43%
2024-06-17 20:00 | 6 | 17 | 20 | 2.057% | 27.22%
2024-06-17 21:00 | 6 | 17 | 21 | 0% | 29.55%
2024-06-17 22:00 | 6 | 17 | 22 | 0% | 31.05%
2024-06-17 23:00 | 6 | 17 | 23 | 0% | 34.67%
2024-06-18 | 6 | 18 | 0 | 0% | 30.88%
2024-06-18 01:00 | 6 | 18 | 1 | 0% | 32.31%
2024-06-18 02:00 | 6 | 18 | 2 | 0% | 32.28%
2024-06-18 03:00 | 6 | 18 | 3 | 0% | 31.42%
2024-06-18 04:00 | 6 | 18 | 4 | 3.362% | 30.15%
2024-06-18 05:00 | 6 | 18 | 5 | 7.784% | 27.54%
2024-06-18 06:00 | 6 | 18 | 6 | 15.93% | 25.94%
2024-06-18 07:00 | 6 | 18 | 7 | 32.99% | 24.74%
2024-06-18 08:00 | 6 | 18 | 8 | 47.99% | 28.13%
2024-06-18 09:00 | 6 | 18 | 9 | 67.04% | 28.05%
2024-06-18 10:00 | 6 | 18 | 10 | 54.58% | 29.56%
2024-06-18 11:00 | 6 | 18 | 11 | 9.14% | 31.62%
2024-06-18 12:00 | 6 | 18 | 12 | 22.61% | 34.06%
2024-06-18 13:00 | 6 | 18 | 13 | 33.19% | 36.23%
2024-06-18 14:00 | 6 | 18 | 14 | 69.99% | 37.13%
2024-06-18 15:00 | 6 | 18 | 15 | 58.13% | 41.08%
2024-06-18 16:00 | 6 | 18 | 16 | 42.34% | 37.15%
2024-06-18 17:00 | 6 | 18 | 17 | 24.78% | 35.17%
2024-06-18 18:00 | 6 | 18 | 18 | 9.294% | 33.37%
2024-06-18 19:00 | 6 | 18 | 19 | 3.621% | 31.41%
2024-06-18 20:00 | 6 | 18 | 20 | 0.3959% | 31.46%
2024-06-18 21:00 | 6 | 18 | 21 | 0% | 30.54%
2024-06-18 22:00 | 6 | 18 | 22 | 0% | 30.61%
2024-06-18 23:00 | 6 | 18 | 23 | 0% | 31.02%
2024-06-19 | 6 | 19 | 0 | 0% | 27.35%
2024-06-19 01:00 | 6 | 19 | 1 | 0% | 30.53%
2024-06-19 02:00 | 6 | 19 | 2 | 0% | 29.92%
2024-06-19 03:00 | 6 | 19 | 3 | 0% | 29.2%
2024-06-19 04:00 | 6 | 19 | 4 | 3.299% | 27.68%
2024-06-19 05:00 | 6 | 19 | 5 | 7.515% | 25.56%
2024-06-19 06:00 | 6 | 19 | 6 | 16.76% | 24.22%
2024-06-19 07:00 | 6 | 19 | 7 | 29.76% | 22.7%
2024-06-19 08:00 | 6 | 19 | 8 | 43.13% | 19.57%
2024-06-19 09:00 | 6 | 19 | 9 | 51.94% | 22.83%
2024-06-19 10:00 | 6 | 19 | 10 | 63.27% | 23.43%
2024-06-19 11:00 | 6 | 19 | 11 | 67.44% | 24.2%
2024-06-19 12:00 | 6 | 19 | 12 | 70.37% | 24.69%
2024-06-19 13:00 | 6 | 19 | 13 | 44.45% | 25.02%
2024-06-19 14:00 | 6 | 19 | 14 | 55.71% | 25.62%
2024-06-19 15:00 | 6 | 19 | 15 | 40.77% | 25.68%
2024-06-19 16:00 | 6 | 19 | 16 | 26.5% | 25.7%
2024-06-19 17:00 | 6 | 19 | 17 | 17.37% | 25.69%
2024-06-19 18:00 | 6 | 19 | 18 | 10.07% | 24.4%
2024-06-19 19:00 | 6 | 19 | 19 | 4.256% | 23.74%
2024-06-19 20:00 | 6 | 19 | 20 | 1.022% | 24.88%
2024-06-19 21:00 | 6 | 19 | 21 | 0% | 26.53%
2024-06-19 22:00 | 6 | 19 | 22 | 0% | 28.18%
2024-06-19 23:00 | 6 | 19 | 23 | 0% | 28.01%
2024-06-20 | 6 | 20 | 0 | 0% | 29.86%
2024-06-20 01:00 | 6 | 20 | 1 | 0% | 26.58%
2024-06-20 02:00 | 6 | 20 | 2 | 0% | 25.46%
2024-06-20 03:00 | 6 | 20 | 3 | 0% | 24.48%
2024-06-20 04:00 | 6 | 20 | 4 | 2.855% | 22.61%
2024-06-20 05:00 | 6 | 20 | 5 | 5.66% | 19.91%
2024-06-20 06:00 | 6 | 20 | 6 | 9.912% | 17.63%
2024-06-20 07:00 | 6 | 20 | 7 | 25.44% | 16.9%
2024-06-20 08:00 | 6 | 20 | 8 | 49.45% | 16.97%
2024-06-20 09:00 | 6 | 20 | 9 | 59.23% | 17.48%
2024-06-20 10:00 | 6 | 20 | 10 | 48.77% | 18.59%
2024-06-20 11:00 | 6 | 20 | 11 | 46.01% | 19.87%
2024-06-20 12:00 | 6 | 20 | 12 | 13.17% | 21.23%
2024-06-20 13:00 | 6 | 20 | 13 | 8.464% | 21.9%
2024-06-20 14:00 | 6 | 20 | 14 | 20.2% | 23.19%
2024-06-20 15:00 | 6 | 20 | 15 | 36.38% | 23.83%
2024-06-20 16:00 | 6 | 20 | 16 | 35.45% | 24.27%
2024-06-20 17:00 | 6 | 20 | 17 | 20.87% | 24.03%
2024-06-20 18:00 | 6 | 20 | 18 | 8.948% | 23.74%
2024-06-20 19:00 | 6 | 20 | 19 | 3.966% | 23.61%
2024-06-20 20:00 | 6 | 20 | 20 | 0.754% | 25.1%
2024-06-20 21:00 | 6 | 20 | 21 | 0% | 26.7%
2024-06-20 22:00 | 6 | 20 | 22 | 0% | 28.32%
2024-06-20 23:00 | 6 | 20 | 23 | 0% | 29.11%
2024-06-21 | 6 | 21 | 0 | 0% | 25.28%
2024-06-21 01:00 | 6 | 21 | 1 | 0% | 29.41%
2024-06-21 02:00 | 6 | 21 | 2 | 0% | 28.28%
2024-06-21 03:00 | 6 | 21 | 3 | 0% | 25.9%
2024-06-21 04:00 | 6 | 21 | 4 | 2.953% | 23.56%
2024-06-21 05:00 | 6 | 21 | 5 | 4.637% | 20.95%
2024-06-21 06:00 | 6 | 21 | 6 | 5.233% | 18.68%
2024-06-21 07:00 | 6 | 21 | 7 | 10.18% | 17.39%
2024-06-21 08:00 | 6 | 21 | 8 | 9.862% | 18.32%
2024-06-21 09:00 | 6 | 21 | 9 | 8.987% | 16.99%
2024-06-21 10:00 | 6 | 21 | 10 | 15.07% | 18.17%
2024-06-21 11:00 | 6 | 21 | 11 | 37.68% | 18.28%
2024-06-21 12:00 | 6 | 21 | 12 | 55.94% | 18.65%
2024-06-21 13:00 | 6 | 21 | 13 | 30.49% | 18.92%
2024-06-21 14:00 | 6 | 21 | 14 | 32.67% | 19.27%
2024-06-21 15:00 | 6 | 21 | 15 | 13.95% | 19.63%
2024-06-21 16:00 | 6 | 21 | 16 | 17.53% | 19.3%
2024-06-21 17:00 | 6 | 21 | 17 | 7.087% | 19.79%
2024-06-21 18:00 | 6 | 21 | 18 | 5.09% | 19.5%
2024-06-21 19:00 | 6 | 21 | 19 | 2.157% | 19.63%
2024-06-21 20:00 | 6 | 21 | 20 | 0% | 19.98%
2024-06-21 21:00 | 6 | 21 | 21 | 0% | 21.23%
2024-06-21 22:00 | 6 | 21 | 22 | 0% | 22.46%
2024-06-21 23:00 | 6 | 21 | 23 | 0% | 24.09%
2024-06-22 | 6 | 22 | 0 | 0% | 21.61%
2024-06-22 01:00 | 6 | 22 | 1 | 0% | 26.21%
2024-06-22 02:00 | 6 | 22 | 2 | 0% | 26.44%
2024-06-22 03:00 | 6 | 22 | 3 | 0% | 26.03%
2024-06-22 04:00 | 6 | 22 | 4 | 3.457% | 25.04%
2024-06-22 05:00 | 6 | 22 | 5 | 7.607% | 23.22%
2024-06-22 06:00 | 6 | 22 | 6 | 10.94% | 21.61%
2024-06-22 07:00 | 6 | 22 | 7 | 15.75% | 20.36%
2024-06-22 08:00 | 6 | 22 | 8 | 25.27% | 19.66%
2024-06-22 09:00 | 6 | 22 | 9 | 43.09% | 19.48%
2024-06-22 10:00 | 6 | 22 | 10 | 36.96% | 19.73%
2024-06-22 11:00 | 6 | 22 | 11 | 49.75% | 21.02%
2024-06-22 12:00 | 6 | 22 | 12 | 67.38% | 21.75%
2024-06-22 13:00 | 6 | 22 | 13 | 66.43% | 22.23%
2024-06-22 14:00 | 6 | 22 | 14 | 67.58% | 22.24%
2024-06-22 15:00 | 6 | 22 | 15 | 62.81% | 22.54%
2024-06-22 16:00 | 6 | 22 | 16 | 46.38% | 21.89%
2024-06-22 17:00 | 6 | 22 | 17 | 27.1% | 20.88%
2024-06-22 18:00 | 6 | 22 | 18 | 9.335% | 20.27%
2024-06-22 19:00 | 6 | 22 | 19 | 4.829% | 19.51%
2024-06-22 20:00 | 6 | 22 | 20 | 1.542% | 19.86%
2024-06-22 21:00 | 6 | 22 | 21 | 0% | 20.75%
2024-06-22 22:00 | 6 | 22 | 22 | 0% | 21.55%
2024-06-22 23:00 | 6 | 22 | 23 | 0% | 22.23%
2024-06-23 | 6 | 23 | 0 | 0% | 20.31%
2024-06-23 01:00 | 6 | 23 | 1 | 0% | 21.3%
2024-06-23 02:00 | 6 | 23 | 2 | 0% | 19.62%
2024-06-23 03:00 | 6 | 23 | 3 | 0% | 18.11%
2024-06-23 04:00 | 6 | 23 | 4 | 3.412% | 16.46%
2024-06-23 05:00 | 6 | 23 | 5 | 6.135% | 14.43%
2024-06-23 06:00 | 6 | 23 | 6 | 17.31% | 12.5%
2024-06-23 07:00 | 6 | 23 | 7 | 28.31% | 11.45%
2024-06-23 08:00 | 6 | 23 | 8 | 57.03% | 11.08%
2024-06-23 09:00 | 6 | 23 | 9 | 64.68% | 11.49%
2024-06-23 10:00 | 6 | 23 | 10 | 75.41% | 11.68%
2024-06-23 11:00 | 6 | 23 | 11 | 75.41% | 13.08%
2024-06-23 12:00 | 6 | 23 | 12 | 75.41% | 12.34%
2024-06-23 13:00 | 6 | 23 | 13 | 75.41% | 12.68%
2024-06-23 14:00 | 6 | 23 | 14 | 75.41% | 13.76%
2024-06-23 15:00 | 6 | 23 | 15 | 63.39% | 13.27%
2024-06-23 16:00 | 6 | 23 | 16 | 34.02% | 14.52%
2024-06-23 17:00 | 6 | 23 | 17 | 19.37% | 14.08%
2024-06-23 18:00 | 6 | 23 | 18 | 10.43% | 14.67%
2024-06-23 19:00 | 6 | 23 | 19 | 5.212% | 16.06%
2024-06-23 20:00 | 6 | 23 | 20 | 1.415% | 17.97%
2024-06-23 21:00 | 6 | 23 | 21 | 0% | 19.66%
2024-06-23 22:00 | 6 | 23 | 22 | 0% | 20.66%
2024-06-23 23:00 | 6 | 23 | 23 | 0% | 20.89%
2024-06-24 | 6 | 24 | 0 | 0% | 21.49%
2024-06-24 01:00 | 6 | 24 | 1 | 0% | 19.12%
2024-06-24 02:00 | 6 | 24 | 2 | 0% | 19.4%
2024-06-24 03:00 | 6 | 24 | 3 | 0% | 17.7%
2024-06-24 04:00 | 6 | 24 | 4 | 3.942% | 16.73%
2024-06-24 05:00 | 6 | 24 | 5 | 6.141% | 15.03%
2024-06-24 06:00 | 6 | 24 | 6 | 20.73% | 13.78%
2024-06-24 07:00 | 6 | 24 | 7 | 40.38% | 13.51%
2024-06-24 08:00 | 6 | 24 | 8 | 58.1% | 13.15%
2024-06-24 09:00 | 6 | 24 | 9 | 71.91% | 13.11%
2024-06-24 10:00 | 6 | 24 | 10 | 75.41% | 13.13%
2024-06-24 11:00 | 6 | 24 | 11 | 75.41% | 15.18%
2024-06-24 12:00 | 6 | 24 | 12 | 75.41% | 14.67%
2024-06-24 13:00 | 6 | 24 | 13 | 75.41% | 16.67%
2024-06-24 14:00 | 6 | 24 | 14 | 69.11% | 15.98%
2024-06-24 15:00 | 6 | 24 | 15 | 56.18% | 16.98%
2024-06-24 16:00 | 6 | 24 | 16 | 29.62% | 19.17%
2024-06-24 17:00 | 6 | 24 | 17 | 19.46% | 18.02%
2024-06-24 18:00 | 6 | 24 | 18 | 9.976% | 17.71%
2024-06-24 19:00 | 6 | 24 | 19 | 4.93% | 18.13%
2024-06-24 20:00 | 6 | 24 | 20 | 0.8616% | 19.11%
2024-06-24 21:00 | 6 | 24 | 21 | 0% | 20.93%
2024-06-24 22:00 | 6 | 24 | 22 | 0% | 22%
2024-06-24 23:00 | 6 | 24 | 23 | 0% | 22.1%
2024-06-25 | 6 | 25 | 0 | 0% | 19.51%
2024-06-25 01:00 | 6 | 25 | 1 | 0% | 20.82%
2024-06-25 02:00 | 6 | 25 | 2 | 0% | 19.58%
2024-06-25 03:00 | 6 | 25 | 3 | 0% | 18.44%
2024-06-25 04:00 | 6 | 25 | 4 | 3.946% | 16.53%
2024-06-25 05:00 | 6 | 25 | 5 | 6.067% | 14.42%
2024-06-25 06:00 | 6 | 25 | 6 | 18.89% | 12.4%
2024-06-25 07:00 | 6 | 25 | 7 | 23.55% | 11.14%
2024-06-25 08:00 | 6 | 25 | 8 | 35.5% | 11.95%
2024-06-25 09:00 | 6 | 25 | 9 | 50.9% | 11.52%
2024-06-25 10:00 | 6 | 25 | 10 | 67.26% | 13.32%
2024-06-25 11:00 | 6 | 25 | 11 | 61.26% | 12.71%
2024-06-25 12:00 | 6 | 25 | 12 | 59.36% | 12.9%
2024-06-25 13:00 | 6 | 25 | 13 | 60.41% | 12.83%
2024-06-25 14:00 | 6 | 25 | 14 | 53.19% | 13.12%
2024-06-25 15:00 | 6 | 25 | 15 | 37.11% | 13.84%
2024-06-25 16:00 | 6 | 25 | 16 | 22.98% | 14%
2024-06-25 17:00 | 6 | 25 | 17 | 17.57% | 13.91%
2024-06-25 18:00 | 6 | 25 | 18 | 10.8% | 13.61%
2024-06-25 19:00 | 6 | 25 | 19 | 4.801% | 14.12%
2024-06-25 20:00 | 6 | 25 | 20 | 0.4126% | 15.68%
2024-06-25 21:00 | 6 | 25 | 21 | 0% | 17.27%
2024-06-25 22:00 | 6 | 25 | 22 | 0% | 18.54%
2024-06-25 23:00 | 6 | 25 | 23 | 0% | 19.52%
2024-06-26 | 6 | 26 | 0 | 0% | 17.22%
2024-06-26 01:00 | 6 | 26 | 1 | 0% | 19.18%
2024-06-26 02:00 | 6 | 26 | 2 | 0% | 18.48%
2024-06-26 03:00 | 6 | 26 | 3 | 0% | 17.45%
2024-06-26 04:00 | 6 | 26 | 4 | 3.04% | 15.7%
2024-06-26 05:00 | 6 | 26 | 5 | 6.944% | 12.47%
2024-06-26 06:00 | 6 | 26 | 6 | 11.41% | 9.853%
2024-06-26 07:00 | 6 | 26 | 7 | 17.21% | 8.617%
2024-06-26 08:00 | 6 | 26 | 8 | 29.92% | 8.696%
2024-06-26 09:00 | 6 | 26 | 9 | 41.32% | 9.281%
2024-06-26 10:00 | 6 | 26 | 10 | 38.34% | 10.18%
2024-06-26 11:00 | 6 | 26 | 11 | 44.77% | 11.72%
2024-06-26 12:00 | 6 | 26 | 12 | 50.35% | 13.45%
2024-06-26 13:00 | 6 | 26 | 13 | 23.58% | 15.86%
2024-06-26 14:00 | 6 | 26 | 14 | 15.47% | 14.85%
2024-06-26 15:00 | 6 | 26 | 15 | 11.14% | 15.1%
2024-06-26 16:00 | 6 | 26 | 16 | 9.025% | 15.16%
2024-06-26 17:00 | 6 | 26 | 17 | 10.41% | 14.56%
2024-06-26 18:00 | 6 | 26 | 18 | 7.415% | 14.32%
2024-06-26 19:00 | 6 | 26 | 19 | 3.53% | 14.31%
2024-06-26 20:00 | 6 | 26 | 20 | 0.5866% | 15.06%
2024-06-26 21:00 | 6 | 26 | 21 | 0% | 16.41%
2024-06-26 22:00 | 6 | 26 | 22 | 0% | 17.46%
2024-06-26 23:00 | 6 | 26 | 23 | 0% | 17.38%
2024-06-27 | 6 | 27 | 0 | 0% | 21.69%
2024-06-27 01:00 | 6 | 27 | 1 | 0% | 16.8%
2024-06-27 02:00 | 6 | 27 | 2 | 0% | 15.86%
2024-06-27 03:00 | 6 | 27 | 3 | 0% | 15.12%
2024-06-27 04:00 | 6 | 27 | 4 | 2.527% | 13.99%
2024-06-27 05:00 | 6 | 27 | 5 | 4.317% | 12.04%
2024-06-27 06:00 | 6 | 27 | 6 | 4.557% | 10.92%
2024-06-27 07:00 | 6 | 27 | 7 | 5.916% | 11%
2024-06-27 08:00 | 6 | 27 | 8 | 11.01% | 12.06%
2024-06-27 09:00 | 6 | 27 | 9 | 11.84% | 13.33%
2024-06-27 10:00 | 6 | 27 | 10 | 15.93% | 14.9%
2024-06-27 11:00 | 6 | 27 | 11 | 21.29% | 16.56%
2024-06-27 12:00 | 6 | 27 | 12 | 20.44% | 18.03%
2024-06-27 13:00 | 6 | 27 | 13 | 19.94% | 18.83%
2024-06-27 14:00 | 6 | 27 | 14 | 16.57% | 18.91%
2024-06-27 15:00 | 6 | 27 | 15 | 23.36% | 19.28%
2024-06-27 16:00 | 6 | 27 | 16 | 23.89% | 19.11%
2024-06-27 17:00 | 6 | 27 | 17 | 20.25% | 18.46%
2024-06-27 18:00 | 6 | 27 | 18 | 9.561% | 17.7%
2024-06-27 19:00 | 6 | 27 | 19 | 4.504% | 18%
2024-06-27 20:00 | 6 | 27 | 20 | 0.9545% | 19.19%
2024-06-27 21:00 | 6 | 27 | 21 | 0% | 20.65%
2024-06-27 22:00 | 6 | 27 | 22 | 0% | 21.83%
2024-06-27 23:00 | 6 | 27 | 23 | 0% | 21.81%
2024-06-28 | 6 | 28 | 0 | 0% | 32.59%
2024-06-28 01:00 | 6 | 28 | 1 | 0% | 20.95%
2024-06-28 02:00 | 6 | 28 | 2 | 0% | 19.75%
2024-06-28 03:00 | 6 | 28 | 3 | 0% | 18.62%
2024-06-28 04:00 | 6 | 28 | 4 | 4.515% | 16.82%
2024-06-28 05:00 | 6 | 28 | 5 | 5.644% | 14.28%
2024-06-28 06:00 | 6 | 28 | 6 | 18.43% | 12.03%
2024-06-28 07:00 | 6 | 28 | 7 | 35.78% | 11.39%
2024-06-28 08:00 | 6 | 28 | 8 | 58.09% | 12.33%
2024-06-28 09:00 | 6 | 28 | 9 | 72.12% | 14.01%
2024-06-28 10:00 | 6 | 28 | 10 | 75.41% | 16.27%
2024-06-28 11:00 | 6 | 28 | 11 | 75.41% | 18.2%
2024-06-28 12:00 | 6 | 28 | 12 | 75.41% | 20.19%
2024-06-28 13:00 | 6 | 28 | 13 | 75.41% | 21.25%
2024-06-28 14:00 | 6 | 28 | 14 | 75.41% | 22.82%
2024-06-28 15:00 | 6 | 28 | 15 | 65.26% | 23.84%
2024-06-28 16:00 | 6 | 28 | 16 | 48.16% | 25.61%
2024-06-28 17:00 | 6 | 28 | 17 | 25.1% | 25%
2024-06-28 18:00 | 6 | 28 | 18 | 10.19% | 26.49%
2024-06-28 19:00 | 6 | 28 | 19 | 4.903% | 25.89%
2024-06-28 20:00 | 6 | 28 | 20 | 1.633% | 27.63%
2024-06-28 21:00 | 6 | 28 | 21 | 0% | 30.24%
2024-06-28 22:00 | 6 | 28 | 22 | 0% | 31.92%
2024-06-28 23:00 | 6 | 28 | 23 | 0% | 33.01%
2024-06-29 | 6 | 29 | 0 | 0% | 27.38%
2024-06-29 01:00 | 6 | 29 | 1 | 0% | 32.03%
2024-06-29 02:00 | 6 | 29 | 2 | 0% | 31.57%
2024-06-29 03:00 | 6 | 29 | 3 | 0% | 30.38%
2024-06-29 04:00 | 6 | 29 | 4 | 3.464% | 28.67%
2024-06-29 05:00 | 6 | 29 | 5 | 8.228% | 27.91%
2024-06-29 06:00 | 6 | 29 | 6 | 13.86% | 26.19%
2024-06-29 07:00 | 6 | 29 | 7 | 21.42% | 26.04%
2024-06-29 08:00 | 6 | 29 | 8 | 52.46% | 26.15%
2024-06-29 09:00 | 6 | 29 | 9 | 72.31% | 27.85%
2024-06-29 10:00 | 6 | 29 | 10 | 75.41% | 27.5%
2024-06-29 11:00 | 6 | 29 | 11 | 75.41% | 26.99%
2024-06-29 12:00 | 6 | 29 | 12 | 75.41% | 27.56%
2024-06-29 13:00 | 6 | 29 | 13 | 75.41% | 27.37%
2024-06-29 14:00 | 6 | 29 | 14 | 67.71% | 27.54%
2024-06-29 15:00 | 6 | 29 | 15 | 56.98% | 29.23%
2024-06-29 16:00 | 6 | 29 | 16 | 45.78% | 28.2%
2024-06-29 17:00 | 6 | 29 | 17 | 24.24% | 27.56%
2024-06-29 18:00 | 6 | 29 | 18 | 9.301% | 27.04%
2024-06-29 19:00 | 6 | 29 | 19 | 2.993% | 26.12%
2024-06-29 20:00 | 6 | 29 | 20 | 0.5808% | 26.41%
2024-06-29 21:00 | 6 | 29 | 21 | 0% | 26.91%
2024-06-29 22:00 | 6 | 29 | 22 | 0% | 27.89%
2024-06-29 23:00 | 6 | 29 | 23 | 0% | 27.44%
2024-06-30 | 6 | 30 | 0 | 0% | 29.51%
2024-06-30 01:00 | 6 | 30 | 1 | 0% | 27.62%
2024-06-30 02:00 | 6 | 30 | 2 | 0% | 27.22%
2024-06-30 03:00 | 6 | 30 | 3 | 0% | 26.07%
2024-06-30 04:00 | 6 | 30 | 4 | 1.239% | 24.53%
2024-06-30 05:00 | 6 | 30 | 5 | 3.509% | 22.62%
2024-06-30 06:00 | 6 | 30 | 6 | 3.709% | 21.31%
2024-06-30 07:00 | 6 | 30 | 7 | 3.944% | 20.67%
2024-06-30 08:00 | 6 | 30 | 8 | 11.31% | 20.92%
2024-06-30 09:00 | 6 | 30 | 9 | 16.87% | 21.66%
2024-06-30 10:00 | 6 | 30 | 10 | 18.56% | 22.47%
2024-06-30 11:00 | 6 | 30 | 11 | 23.09% | 23.56%
2024-06-30 12:00 | 6 | 30 | 12 | 34.86% | 27.08%
2024-06-30 13:00 | 6 | 30 | 13 | 38.38% | 27.14%
2024-06-30 14:00 | 6 | 30 | 14 | 58.52% | 28.03%
2024-06-30 15:00 | 6 | 30 | 15 | 38.16% | 31.12%
2024-06-30 16:00 | 6 | 30 | 16 | 17.53% | 31.25%
2024-06-30 17:00 | 6 | 30 | 17 | 14.92% | 28.43%
2024-06-30 18:00 | 6 | 30 | 18 | 8.277% | 27.86%
2024-06-30 19:00 | 6 | 30 | 19 | 3.658% | 26.88%
2024-06-30 20:00 | 6 | 30 | 20 | 0.4909% | 26.86%
2024-06-30 21:00 | 6 | 30 | 21 | 0% | 27.95%
2024-06-30 22:00 | 6 | 30 | 22 | 0% | 28.76%
2024-06-30 23:00 | 6 | 30 | 23 | 0% | 29.52%
2024-07-01 | 7 | 1 | 0 | 0% | 25.96%
2024-07-01 01:00 | 7 | 1 | 1 | 0% | 29.1%
2024-07-01 02:00 | 7 | 1 | 2 | 0% | 28.56%
2024-07-01 03:00 | 7 | 1 | 3 | 0% | 27.99%
2024-07-01 04:00 | 7 | 1 | 4 | 1.322% | 26.55%
2024-07-01 05:00 | 7 | 1 | 5 | 1.123% | 24.47%
2024-07-01 06:00 | 7 | 1 | 6 | 6.791% | 22.82%
2024-07-01 07:00 | 7 | 1 | 7 | 23.15% | 22.15%
2024-07-01 08:00 | 7 | 1 | 8 | 52.75% | 23.08%
2024-07-01 09:00 | 7 | 1 | 9 | 52.44% | 24.77%
2024-07-01 10:00 | 7 | 1 | 10 | 47.09% | 26.11%
2024-07-01 11:00 | 7 | 1 | 11 | 74.62% | 27.13%
2024-07-01 12:00 | 7 | 1 | 12 | 64.97% | 27.91%
2024-07-01 13:00 | 7 | 1 | 13 | 72.87% | 28.44%
2024-07-01 14:00 | 7 | 1 | 14 | 25.59% | 28.89%
2024-07-01 15:00 | 7 | 1 | 15 | 41.27% | 29.38%
2024-07-01 16:00 | 7 | 1 | 16 | 23.38% | 29.12%
2024-07-01 17:00 | 7 | 1 | 17 | 20.04% | 27.75%
2024-07-01 18:00 | 7 | 1 | 18 | 10.23% | 25.9%
2024-07-01 19:00 | 7 | 1 | 19 | 4.333% | 24.29%
2024-07-01 20:00 | 7 | 1 | 20 | 2.397% | 24.19%
2024-07-01 21:00 | 7 | 1 | 21 | 0% | 25.27%
2024-07-01 22:00 | 7 | 1 | 22 | 0% | 26.02%
2024-07-01 23:00 | 7 | 1 | 23 | 0% | 25.88%
2024-07-02 | 7 | 2 | 0 | 0% | 27.35%
2024-07-02 01:00 | 7 | 2 | 1 | 0% | 25.25%
2024-07-02 02:00 | 7 | 2 | 2 | 0% | 26.31%
2024-07-02 03:00 | 7 | 2 | 3 | 0% | 25.36%
2024-07-02 04:00 | 7 | 2 | 4 | 0.8732% | 26.45%
2024-07-02 05:00 | 7 | 2 | 5 | 5.161% | 23.53%
2024-07-02 06:00 | 7 | 2 | 6 | 8.767% | 22.78%
2024-07-02 07:00 | 7 | 2 | 7 | 13.7% | 22.51%
2024-07-02 08:00 | 7 | 2 | 8 | 8.096% | 24.06%
2024-07-02 09:00 | 7 | 2 | 9 | 24.26% | 26.3%
2024-07-02 10:00 | 7 | 2 | 10 | 55.21% | 28%
2024-07-02 11:00 | 7 | 2 | 11 | 75.41% | 31.16%
2024-07-02 12:00 | 7 | 2 | 12 | 75.41% | 31.27%
2024-07-02 13:00 | 7 | 2 | 13 | 75.41% | 31.67%
2024-07-02 14:00 | 7 | 2 | 14 | 32.4% | 31.44%
2024-07-02 15:00 | 7 | 2 | 15 | 34.71% | 31.36%
2024-07-02 16:00 | 7 | 2 | 16 | 20.27% | 30.71%
2024-07-02 17:00 | 7 | 2 | 17 | 21.51% | 29.36%
2024-07-02 18:00 | 7 | 2 | 18 | 10.21% | 27.35%
2024-07-02 19:00 | 7 | 2 | 19 | 5.175% | 25.75%
2024-07-02 20:00 | 7 | 2 | 20 | 1.22% | 25.3%
2024-07-02 21:00 | 7 | 2 | 21 | 0% | 25.93%
2024-07-02 22:00 | 7 | 2 | 22 | 0% | 27.01%
2024-07-02 23:00 | 7 | 2 | 23 | 0% | 26.89%
2024-07-03 | 7 | 3 | 0 | 0% | 28.91%
2024-07-03 01:00 | 7 | 3 | 1 | 0% | 27.91%
2024-07-03 02:00 | 7 | 3 | 2 | 0% | 28.26%
2024-07-03 03:00 | 7 | 3 | 3 | 0% | 28.73%
2024-07-03 04:00 | 7 | 3 | 4 | 1.596% | 28.2%
2024-07-03 05:00 | 7 | 3 | 5 | 5.888% | 27.01%
2024-07-03 06:00 | 7 | 3 | 6 | 20.65% | 26.26%
2024-07-03 07:00 | 7 | 3 | 7 | 40.85% | 26.73%
2024-07-03 08:00 | 7 | 3 | 8 | 59.01% | 27.77%
2024-07-03 09:00 | 7 | 3 | 9 | 73.4% | 28.62%
2024-07-03 10:00 | 7 | 3 | 10 | 75.41% | 29.96%
2024-07-03 11:00 | 7 | 3 | 11 | 75.41% | 30.88%
2024-07-03 12:00 | 7 | 3 | 12 | 75.41% | 31.56%
2024-07-03 13:00 | 7 | 3 | 13 | 75.41% | 32.86%
2024-07-03 14:00 | 7 | 3 | 14 | 55.68% | 33.58%
2024-07-03 15:00 | 7 | 3 | 15 | 62.27% | 33.44%
2024-07-03 16:00 | 7 | 3 | 16 | 39.87% | 31.69%
2024-07-03 17:00 | 7 | 3 | 17 | 11.25% | 31.36%
2024-07-03 18:00 | 7 | 3 | 18 | 5.984% | 29.04%
2024-07-03 19:00 | 7 | 3 | 19 | 3.995% | 27.29%
2024-07-03 20:00 | 7 | 3 | 20 | 1.696% | 27.63%
2024-07-03 21:00 | 7 | 3 | 21 | 0% | 28.92%
2024-07-03 22:00 | 7 | 3 | 22 | 0% | 29.67%
2024-07-03 23:00 | 7 | 3 | 23 | 0% | 29.27%
2024-07-04 | 7 | 4 | 0 | 0% | 30.38%
2024-07-04 01:00 | 7 | 4 | 1 | 0% | 28.06%
2024-07-04 02:00 | 7 | 4 | 2 | 0% | 27.38%
2024-07-04 03:00 | 7 | 4 | 3 | 0% | 26.79%
2024-07-04 04:00 | 7 | 4 | 4 | 2.747% | 25.11%
2024-07-04 05:00 | 7 | 4 | 5 | 5.626% | 22.76%
2024-07-04 06:00 | 7 | 4 | 6 | 20.24% | 21.21%
2024-07-04 07:00 | 7 | 4 | 7 | 38.54% | 20.88%
2024-07-04 08:00 | 7 | 4 | 8 | 43.39% | 21.28%
2024-07-04 09:00 | 7 | 4 | 9 | 63.01% | 22.74%
2024-07-04 10:00 | 7 | 4 | 10 | 75.19% | 24.05%
2024-07-04 11:00 | 7 | 4 | 11 | 75.41% | 25.54%
2024-07-04 12:00 | 7 | 4 | 12 | 75.41% | 26.28%
2024-07-04 13:00 | 7 | 4 | 13 | 75.41% | 29.11%
2024-07-04 14:00 | 7 | 4 | 14 | 75.41% | 27.76%
2024-07-04 15:00 | 7 | 4 | 15 | 65.94% | 28.24%
2024-07-04 16:00 | 7 | 4 | 16 | 48.82% | 27.62%
2024-07-04 17:00 | 7 | 4 | 17 | 28.78% | 26.54%
2024-07-04 18:00 | 7 | 4 | 18 | 10.48% | 25.09%
2024-07-04 19:00 | 7 | 4 | 19 | 4.805% | 24.85%
2024-07-04 20:00 | 7 | 4 | 20 | 2.482% | 25.28%
2024-07-04 21:00 | 7 | 4 | 21 | 0% | 27.35%
2024-07-04 22:00 | 7 | 4 | 22 | 0% | 29.08%
2024-07-04 23:00 | 7 | 4 | 23 | 0% | 32.17%
2024-07-05 | 7 | 5 | 0 | 0% | 32.45%
2024-07-05 01:00 | 7 | 5 | 1 | 0% | 31.86%
2024-07-05 02:00 | 7 | 5 | 2 | 0% | 29.2%
2024-07-05 03:00 | 7 | 5 | 3 | 0% | 28.02%
2024-07-05 04:00 | 7 | 5 | 4 | 2.038% | 26.49%
2024-07-05 05:00 | 7 | 5 | 5 | 4.899% | 24.79%
2024-07-05 06:00 | 7 | 5 | 6 | 18.92% | 23.64%
2024-07-05 07:00 | 7 | 5 | 7 | 27.03% | 23.02%
2024-07-05 08:00 | 7 | 5 | 8 | 54.99% | 23.62%
2024-07-05 09:00 | 7 | 5 | 9 | 72.06% | 24.73%
2024-07-05 10:00 | 7 | 5 | 10 | 75.41% | 25.97%
2024-07-05 11:00 | 7 | 5 | 11 | 75.41% | 26.98%
2024-07-05 12:00 | 7 | 5 | 12 | 75.41% | 27.91%
2024-07-05 13:00 | 7 | 5 | 13 | 75.41% | 28.91%
2024-07-05 14:00 | 7 | 5 | 14 | 75.41% | 29.42%
2024-07-05 15:00 | 7 | 5 | 15 | 65.93% | 30.29%
2024-07-05 16:00 | 7 | 5 | 16 | 48.6% | 29.66%
2024-07-05 17:00 | 7 | 5 | 17 | 28.45% | 28.5%
2024-07-05 18:00 | 7 | 5 | 18 | 9.989% | 27.71%
2024-07-05 19:00 | 7 | 5 | 19 | 4.78% | 27.78%
2024-07-05 20:00 | 7 | 5 | 20 | 2.238% | 28.82%
2024-07-05 21:00 | 7 | 5 | 21 | 0% | 30.21%
2024-07-05 22:00 | 7 | 5 | 22 | 0% | 26.34%
2024-07-05 23:00 | 7 | 5 | 23 | 0% | 32.47%
2024-07-06 | 7 | 6 | 0 | 0% | 31.34%
2024-07-06 01:00 | 7 | 6 | 1 | 0% | 31.84%
2024-07-06 02:00 | 7 | 6 | 2 | 0% | 31.35%
2024-07-06 03:00 | 7 | 6 | 3 | 0% | 30.76%
2024-07-06 04:00 | 7 | 6 | 4 | 1.223% | 29.47%
2024-07-06 05:00 | 7 | 6 | 5 | 5.639% | 27.61%
2024-07-06 06:00 | 7 | 6 | 6 | 20.18% | 26.79%
2024-07-06 07:00 | 7 | 6 | 7 | 38.6% | 25.81%
2024-07-06 08:00 | 7 | 6 | 8 | 54.2% | 25.39%
2024-07-06 09:00 | 7 | 6 | 9 | 72.56% | 25.24%
2024-07-06 10:00 | 7 | 6 | 10 | 75.41% | 27.57%
2024-07-06 11:00 | 7 | 6 | 11 | 75.41% | 26.21%
2024-07-06 12:00 | 7 | 6 | 12 | 75.41% | 26.49%
2024-07-06 13:00 | 7 | 6 | 13 | 75.41% | 27.7%
2024-07-06 14:00 | 7 | 6 | 14 | 61.6% | 28.72%
2024-07-06 15:00 | 7 | 6 | 15 | 57.98% | 29.41%
2024-07-06 16:00 | 7 | 6 | 16 | 43.99% | 29.79%
2024-07-06 17:00 | 7 | 6 | 17 | 26.65% | 29.82%
2024-07-06 18:00 | 7 | 6 | 18 | 11.5% | 28.65%
2024-07-06 19:00 | 7 | 6 | 19 | 3.921% | 28.15%
2024-07-06 20:00 | 7 | 6 | 20 | 1.224% | 28.65%
2024-07-06 21:00 | 7 | 6 | 21 | 0% | 29.55%
2024-07-06 22:00 | 7 | 6 | 22 | 0% | 30.81%
2024-07-06 23:00 | 7 | 6 | 23 | 0% | 30.9%
2024-07-07 | 7 | 7 | 0 | 0% | 23.96%
2024-07-07 01:00 | 7 | 7 | 1 | 0% | 31.45%
2024-07-07 02:00 | 7 | 7 | 2 | 0% | 31.35%
2024-07-07 03:00 | 7 | 7 | 3 | 0% | 31.06%
2024-07-07 04:00 | 7 | 7 | 4 | 0% | 30.4%
2024-07-07 05:00 | 7 | 7 | 5 | 3.167% | 30.03%
2024-07-07 06:00 | 7 | 7 | 6 | 6.644% | 29.66%
2024-07-07 07:00 | 7 | 7 | 7 | 13.74% | 29.63%
2024-07-07 08:00 | 7 | 7 | 8 | 21.47% | 28.59%
2024-07-07 09:00 | 7 | 7 | 9 | 49.34% | 29.08%
2024-07-07 10:00 | 7 | 7 | 10 | 73.49% | 29.82%
2024-07-07 11:00 | 7 | 7 | 11 | 75.41% | 30.43%
2024-07-07 12:00 | 7 | 7 | 12 | 70.56% | 30.56%
2024-07-07 13:00 | 7 | 7 | 13 | 26.21% | 30.74%
2024-07-07 14:00 | 7 | 7 | 14 | 24.2% | 30.42%
2024-07-07 15:00 | 7 | 7 | 15 | 17.78% | 30.44%
2024-07-07 16:00 | 7 | 7 | 16 | 12.05% | 30.27%
2024-07-07 17:00 | 7 | 7 | 17 | 8.649% | 28.6%
2024-07-07 18:00 | 7 | 7 | 18 | 9.082% | 26.44%
2024-07-07 19:00 | 7 | 7 | 19 | 4.186% | 24.53%
2024-07-07 20:00 | 7 | 7 | 20 | 0.4126% | 23.82%
2024-07-07 21:00 | 7 | 7 | 21 | 0% | 24.49%
2024-07-07 22:00 | 7 | 7 | 22 | 0% | 25.03%
2024-07-07 23:00 | 7 | 7 | 23 | 0% | 24.47%
2024-07-08 | 7 | 8 | 0 | 0% | 17.68%
2024-07-08 01:00 | 7 | 8 | 1 | 0% | 23.38%
2024-07-08 02:00 | 7 | 8 | 2 | 0% | 22.17%
2024-07-08 03:00 | 7 | 8 | 3 | 0% | 20.98%
2024-07-08 04:00 | 7 | 8 | 4 | 0.6153% | 19.25%
2024-07-08 05:00 | 7 | 8 | 5 | 5.614% | 17.03%
2024-07-08 06:00 | 7 | 8 | 6 | 8.51% | 14.79%
2024-07-08 07:00 | 7 | 8 | 7 | 16.54% | 13.18%
2024-07-08 08:00 | 7 | 8 | 8 | 13.68% | 12.66%
2024-07-08 09:00 | 7 | 8 | 9 | 20.51% | 12.83%
2024-07-08 10:00 | 7 | 8 | 10 | 40.71% | 13.17%
2024-07-08 11:00 | 7 | 8 | 11 | 46.81% | 13.57%
2024-07-08 12:00 | 7 | 8 | 12 | 53.42% | 14.21%
2024-07-08 13:00 | 7 | 8 | 13 | 39.82% | 13.21%
2024-07-08 14:00 | 7 | 8 | 14 | 20.25% | 13.91%
2024-07-08 15:00 | 7 | 8 | 15 | 41.05% | 13.12%
2024-07-08 16:00 | 7 | 8 | 16 | 35.62% | 12.86%
2024-07-08 17:00 | 7 | 8 | 17 | 28.03% | 12.16%
2024-07-08 18:00 | 7 | 8 | 18 | 10.64% | 11.24%
2024-07-08 19:00 | 7 | 8 | 19 | 4.969% | 11.46%
2024-07-08 20:00 | 7 | 8 | 20 | 1.757% | 12.61%
2024-07-08 21:00 | 7 | 8 | 21 | 0% | 14.78%
2024-07-08 22:00 | 7 | 8 | 22 | 0% | 16.35%
2024-07-08 23:00 | 7 | 8 | 23 | 0% | 16.92%
2024-07-09 | 7 | 9 | 0 | 0% | 21.23%
2024-07-09 01:00 | 7 | 9 | 1 | 0% | 17.78%
2024-07-09 02:00 | 7 | 9 | 2 | 0% | 17.44%
2024-07-09 03:00 | 7 | 9 | 3 | 0% | 17.02%
2024-07-09 04:00 | 7 | 9 | 4 | 0.9756% | 15.8%
2024-07-09 05:00 | 7 | 9 | 5 | 5.502% | 13.79%
2024-07-09 06:00 | 7 | 9 | 6 | 18.75% | 12.18%
2024-07-09 07:00 | 7 | 9 | 7 | 37.66% | 11.45%
2024-07-09 08:00 | 7 | 9 | 8 | 57.63% | 11.54%
2024-07-09 09:00 | 7 | 9 | 9 | 61.85% | 11.77%
2024-07-09 10:00 | 7 | 9 | 10 | 48.23% | 12.84%
2024-07-09 11:00 | 7 | 9 | 11 | 55.59% | 13.78%
2024-07-09 12:00 | 7 | 9 | 12 | 55.3% | 15.06%
2024-07-09 13:00 | 7 | 9 | 13 | 35.03% | 16.06%
2024-07-09 14:00 | 7 | 9 | 14 | 58.83% | 17.37%
2024-07-09 15:00 | 7 | 9 | 15 | 64.33% | 17.96%
2024-07-09 16:00 | 7 | 9 | 16 | 47.58% | 17.43%
2024-07-09 17:00 | 7 | 9 | 17 | 27.89% | 16.62%
2024-07-09 18:00 | 7 | 9 | 18 | 9.951% | 15.71%
2024-07-09 19:00 | 7 | 9 | 19 | 3.868% | 15.08%
2024-07-09 20:00 | 7 | 9 | 20 | 1.909% | 15.61%
2024-07-09 21:00 | 7 | 9 | 21 | 0% | 16.78%
2024-07-09 22:00 | 7 | 9 | 22 | 0% | 18.14%
2024-07-09 23:00 | 7 | 9 | 23 | 0% | 19.8%
2024-07-10 | 7 | 10 | 0 | 0% | 17.34%
2024-07-10 01:00 | 7 | 10 | 1 | 0% | 21.96%
2024-07-10 02:00 | 7 | 10 | 2 | 0% | 22.1%
2024-07-10 03:00 | 7 | 10 | 3 | 0% | 22.67%
2024-07-10 04:00 | 7 | 10 | 4 | 2.998% | 22.38%
2024-07-10 05:00 | 7 | 10 | 5 | 6.451% | 21.45%
2024-07-10 06:00 | 7 | 10 | 6 | 19.2% | 20.31%
2024-07-10 07:00 | 7 | 10 | 7 | 33.84% | 19.97%
2024-07-10 08:00 | 7 | 10 | 8 | 43.52% | 19.88%
2024-07-10 09:00 | 7 | 10 | 9 | 52.21% | 22.29%
2024-07-10 10:00 | 7 | 10 | 10 | 60.47% | 20.43%
2024-07-10 11:00 | 7 | 10 | 11 | 66.95% | 20.11%
2024-07-10 12:00 | 7 | 10 | 12 | 40.32% | 19.71%
2024-07-10 13:00 | 7 | 10 | 13 | 23.29% | 19.32%
2024-07-10 14:00 | 7 | 10 | 14 | 23.45% | 18.92%
2024-07-10 15:00 | 7 | 10 | 15 | 23.77% | 18.69%
2024-07-10 16:00 | 7 | 10 | 16 | 18.24% | 17.53%
2024-07-10 17:00 | 7 | 10 | 17 | 7.793% | 16.89%
2024-07-10 18:00 | 7 | 10 | 18 | 4.804% | 15.67%
2024-07-10 19:00 | 7 | 10 | 19 | 2.128% | 15.61%
2024-07-10 20:00 | 7 | 10 | 20 | 0.6831% | 15.99%
2024-07-10 21:00 | 7 | 10 | 21 | 0% | 17.11%
2024-07-10 22:00 | 7 | 10 | 22 | 0% | 17.62%
2024-07-10 23:00 | 7 | 10 | 23 | 0% | 17.61%
2024-07-11 | 7 | 11 | 0 | 0% | 22.63%
2024-07-11 01:00 | 7 | 11 | 1 | 0% | 17.24%
2024-07-11 02:00 | 7 | 11 | 2 | 0% | 16.8%
2024-07-11 03:00 | 7 | 11 | 3 | 0% | 16.99%
2024-07-11 04:00 | 7 | 11 | 4 | 2.979% | 16.89%
2024-07-11 05:00 | 7 | 11 | 5 | 5.497% | 15.7%
2024-07-11 06:00 | 7 | 11 | 6 | 18.63% | 13.84%
2024-07-11 07:00 | 7 | 11 | 7 | 35.88% | 12.8%
2024-07-11 08:00 | 7 | 11 | 8 | 52.69% | 13%
2024-07-11 09:00 | 7 | 11 | 9 | 45.12% | 14.24%
2024-07-11 10:00 | 7 | 11 | 10 | 50.52% | 16.62%
2024-07-11 11:00 | 7 | 11 | 11 | 44.98% | 16.67%
2024-07-11 12:00 | 7 | 11 | 12 | 27.41% | 17.57%
2024-07-11 13:00 | 7 | 11 | 13 | 21.48% | 18.59%
2024-07-11 14:00 | 7 | 11 | 14 | 13.32% | 19.34%
2024-07-11 15:00 | 7 | 11 | 15 | 30.21% | 19.6%
2024-07-11 16:00 | 7 | 11 | 16 | 15.4% | 19.77%
2024-07-11 17:00 | 7 | 11 | 17 | 17.77% | 19.09%
2024-07-11 18:00 | 7 | 11 | 18 | 8.852% | 18.32%
2024-07-11 19:00 | 7 | 11 | 19 | 3.806% | 18.24%
2024-07-11 20:00 | 7 | 11 | 20 | 0.7763% | 19.54%
2024-07-11 21:00 | 7 | 11 | 21 | 0% | 21.07%
2024-07-11 22:00 | 7 | 11 | 22 | 0% | 24.25%
2024-07-11 23:00 | 7 | 11 | 23 | 0% | 22.91%
2024-07-12 | 7 | 12 | 0 | 0% | 20.87%
2024-07-12 01:00 | 7 | 12 | 1 | 0% | 22.09%
2024-07-12 02:00 | 7 | 12 | 2 | 0% | 21.51%
2024-07-12 03:00 | 7 | 12 | 3 | 0% | 20.93%
2024-07-12 04:00 | 7 | 12 | 4 | 0.9649% | 19.99%
2024-07-12 05:00 | 7 | 12 | 5 | 2.551% | 18.99%
2024-07-12 06:00 | 7 | 12 | 6 | 14.63% | 18.03%
2024-07-12 07:00 | 7 | 12 | 7 | 21.92% | 17.39%
2024-07-12 08:00 | 7 | 12 | 8 | 38.97% | 17.13%
2024-07-12 09:00 | 7 | 12 | 9 | 59.06% | 18.77%
2024-07-12 10:00 | 7 | 12 | 10 | 66.59% | 19.49%
2024-07-12 11:00 | 7 | 12 | 11 | 60.17% | 19.62%
2024-07-12 12:00 | 7 | 12 | 12 | 56.5% | 18.02%
2024-07-12 13:00 | 7 | 12 | 13 | 67.69% | 19.78%
2024-07-12 14:00 | 7 | 12 | 14 | 69.13% | 19.24%
2024-07-12 15:00 | 7 | 12 | 15 | 58.38% | 19.61%
2024-07-12 16:00 | 7 | 12 | 16 | 36.41% | 18.88%
2024-07-12 17:00 | 7 | 12 | 17 | 22.36% | 18.47%
2024-07-12 18:00 | 7 | 12 | 18 | 9.767% | 19.31%
2024-07-12 19:00 | 7 | 12 | 19 | 3.833% | 17.73%
2024-07-12 20:00 | 7 | 12 | 20 | 2.441% | 18.49%
2024-07-12 21:00 | 7 | 12 | 21 | 0% | 19.76%
2024-07-12 22:00 | 7 | 12 | 22 | 0% | 20.72%
2024-07-12 23:00 | 7 | 12 | 23 | 0% | 21.42%
2024-07-13 | 7 | 13 | 0 | 0% | 23.84%
2024-07-13 01:00 | 7 | 13 | 1 | 0% | 21.61%
2024-07-13 02:00 | 7 | 13 | 2 | 0% | 20.44%
2024-07-13 03:00 | 7 | 13 | 3 | 0% | 19.85%
2024-07-13 04:00 | 7 | 13 | 4 | 4.312% | 18.63%
2024-07-13 05:00 | 7 | 13 | 5 | 4.96% | 17.12%
2024-07-13 06:00 | 7 | 13 | 6 | 19.05% | 15.8%
2024-07-13 07:00 | 7 | 13 | 7 | 39.57% | 15.23%
2024-07-13 08:00 | 7 | 13 | 8 | 58% | 17.52%
2024-07-13 09:00 | 7 | 13 | 9 | 72.47% | 17.73%
2024-07-13 10:00 | 7 | 13 | 10 | 75.41% | 19.36%
2024-07-13 11:00 | 7 | 13 | 11 | 75.41% | 21.18%
2024-07-13 12:00 | 7 | 13 | 12 | 75.41% | 22.76%
2024-07-13 13:00 | 7 | 13 | 13 | 75.41% | 23.75%
2024-07-13 14:00 | 7 | 13 | 14 | 69.26% | 23.98%
2024-07-13 15:00 | 7 | 13 | 15 | 62.2% | 23.85%
2024-07-13 16:00 | 7 | 13 | 16 | 46.64% | 22.83%
2024-07-13 17:00 | 7 | 13 | 17 | 20.95% | 22.59%
2024-07-13 18:00 | 7 | 13 | 18 | 10.52% | 21.58%
2024-07-13 19:00 | 7 | 13 | 19 | 4.212% | 21.3%
2024-07-13 20:00 | 7 | 13 | 20 | 2.149% | 22.02%
2024-07-13 21:00 | 7 | 13 | 21 | 0% | 23.86%
2024-07-13 22:00 | 7 | 13 | 22 | 0% | 25.02%
2024-07-13 23:00 | 7 | 13 | 23 | 0% | 23.91%
2024-07-14 | 7 | 14 | 0 | 0% | 15.62%
2024-07-14 01:00 | 7 | 14 | 1 | 0% | 23.06%
2024-07-14 02:00 | 7 | 14 | 2 | 0% | 21.82%
2024-07-14 03:00 | 7 | 14 | 3 | 0% | 20.75%
2024-07-14 04:00 | 7 | 14 | 4 | 0.7964% | 19.35%
2024-07-14 05:00 | 7 | 14 | 5 | 5.228% | 17.28%
2024-07-14 06:00 | 7 | 14 | 6 | 13.34% | 15.61%
2024-07-14 07:00 | 7 | 14 | 7 | 25.23% | 14.64%
2024-07-14 08:00 | 7 | 14 | 8 | 35.94% | 14.43%
2024-07-14 09:00 | 7 | 14 | 9 | 40.58% | 15.01%
2024-07-14 10:00 | 7 | 14 | 10 | 49.38% | 15.24%
2024-07-14 11:00 | 7 | 14 | 11 | 57.59% | 15.64%
2024-07-14 12:00 | 7 | 14 | 12 | 28.38% | 15.63%
2024-07-14 13:00 | 7 | 14 | 13 | 41.6% | 15.88%
2024-07-14 14:00 | 7 | 14 | 14 | 43.37% | 15.78%
2024-07-14 15:00 | 7 | 14 | 15 | 33.55% | 15.56%
2024-07-14 16:00 | 7 | 14 | 16 | 22.28% | 14.8%
2024-07-14 17:00 | 7 | 14 | 17 | 22.08% | 13.9%
2024-07-14 18:00 | 7 | 14 | 18 | 7.719% | 12.7%
2024-07-14 19:00 | 7 | 14 | 19 | 3.951% | 13%
2024-07-14 20:00 | 7 | 14 | 20 | 0.9477% | 12.48%
2024-07-14 21:00 | 7 | 14 | 21 | 0% | 13.65%
2024-07-14 22:00 | 7 | 14 | 22 | 0% | 14.5%
2024-07-14 23:00 | 7 | 14 | 23 | 0% | 15.39%
2024-07-15 | 7 | 15 | 0 | 0% | 21.13%
2024-07-15 01:00 | 7 | 15 | 1 | 0% | 15.13%
2024-07-15 02:00 | 7 | 15 | 2 | 0% | 14.79%
2024-07-15 03:00 | 7 | 15 | 3 | 0% | 14.56%
2024-07-15 04:00 | 7 | 15 | 4 | 3.318% | 13.74%
2024-07-15 05:00 | 7 | 15 | 5 | 4.89% | 12.08%
2024-07-15 06:00 | 7 | 15 | 6 | 18.08% | 10.46%
2024-07-15 07:00 | 7 | 15 | 7 | 37.89% | 9.787%
2024-07-15 08:00 | 7 | 15 | 8 | 56% | 10.27%
2024-07-15 09:00 | 7 | 15 | 9 | 70.2% | 11.23%
2024-07-15 10:00 | 7 | 15 | 10 | 75.41% | 12.42%
2024-07-15 11:00 | 7 | 15 | 11 | 75.41% | 14.36%
2024-07-15 12:00 | 7 | 15 | 12 | 75.41% | 14.99%
2024-07-15 13:00 | 7 | 15 | 13 | 75.41% | 15.98%
2024-07-15 14:00 | 7 | 15 | 14 | 75.41% | 16.64%
2024-07-15 15:00 | 7 | 15 | 15 | 64.44% | 16.92%
2024-07-15 16:00 | 7 | 15 | 16 | 47.39% | 16.5%
2024-07-15 17:00 | 7 | 15 | 17 | 27.51% | 16.29%
2024-07-15 18:00 | 7 | 15 | 18 | 9.325% | 15.51%
2024-07-15 19:00 | 7 | 15 | 19 | 4.03% | 15.25%
2024-07-15 20:00 | 7 | 15 | 20 | 0.7416% | 16.33%
2024-07-15 21:00 | 7 | 15 | 21 | 0% | 18.29%
2024-07-15 22:00 | 7 | 15 | 22 | 0% | 19.51%
2024-07-15 23:00 | 7 | 15 | 23 | 0% | 20.26%
2024-07-16 | 7 | 16 | 0 | 0% | 28.12%
2024-07-16 01:00 | 7 | 16 | 1 | 0% | 21.04%
2024-07-16 02:00 | 7 | 16 | 2 | 0% | 21.3%
2024-07-16 03:00 | 7 | 16 | 3 | 0% | 21.8%
2024-07-16 04:00 | 7 | 16 | 4 | 1.49% | 21.55%
2024-07-16 05:00 | 7 | 16 | 5 | 1.929% | 19.6%
2024-07-16 06:00 | 7 | 16 | 6 | 8.31% | 19.27%
2024-07-16 07:00 | 7 | 16 | 7 | 11.89% | 19.26%
2024-07-16 08:00 | 7 | 16 | 8 | 10.9% | 22.09%
2024-07-16 09:00 | 7 | 16 | 9 | 10.65% | 21.4%
2024-07-16 10:00 | 7 | 16 | 10 | 11.47% | 23.02%
2024-07-16 11:00 | 7 | 16 | 11 | 9.776% | 23.83%
2024-07-16 12:00 | 7 | 16 | 12 | 11.58% | 24.56%
2024-07-16 13:00 | 7 | 16 | 13 | 14.77% | 25.45%
2024-07-16 14:00 | 7 | 16 | 14 | 16.46% | 26.11%
2024-07-16 15:00 | 7 | 16 | 15 | 18.11% | 27%
2024-07-16 16:00 | 7 | 16 | 16 | 33.94% | 27.22%
2024-07-16 17:00 | 7 | 16 | 17 | 26.24% | 29.07%
2024-07-16 18:00 | 7 | 16 | 18 | 10.49% | 27.83%
2024-07-16 19:00 | 7 | 16 | 19 | 4.888% | 24.82%
2024-07-16 20:00 | 7 | 16 | 20 | 1.077% | 25.67%
2024-07-16 21:00 | 7 | 16 | 21 | 0% | 26.76%
2024-07-16 22:00 | 7 | 16 | 22 | 0% | 27.87%
2024-07-16 23:00 | 7 | 16 | 23 | 0% | 28.2%
2024-07-17 | 7 | 17 | 0 | 0% | 32.64%
2024-07-17 01:00 | 7 | 17 | 1 | 0% | 29.77%
2024-07-17 02:00 | 7 | 17 | 2 | 0% | 27.96%
2024-07-17 03:00 | 7 | 17 | 3 | 0% | 27.85%
2024-07-17 04:00 | 7 | 17 | 4 | 3.571% | 27.01%
2024-07-17 05:00 | 7 | 17 | 5 | 4.702% | 25.3%
2024-07-17 06:00 | 7 | 17 | 6 | 18.27% | 23.77%
2024-07-17 07:00 | 7 | 17 | 7 | 35.44% | 23.43%
2024-07-17 08:00 | 7 | 17 | 8 | 56.67% | 23.27%
2024-07-17 09:00 | 7 | 17 | 9 | 67.46% | 23.69%
2024-07-17 10:00 | 7 | 17 | 10 | 75.41% | 24.57%
2024-07-17 11:00 | 7 | 17 | 11 | 75.41% | 25.4%
2024-07-17 12:00 | 7 | 17 | 12 | 75.41% | 28.56%
2024-07-17 13:00 | 7 | 17 | 13 | 75.41% | 27.5%
2024-07-17 14:00 | 7 | 17 | 14 | 75.41% | 27.84%
2024-07-17 15:00 | 7 | 17 | 15 | 64.57% | 28.84%
2024-07-17 16:00 | 7 | 17 | 16 | 47.23% | 29.25%
2024-07-17 17:00 | 7 | 17 | 17 | 25.5% | 28.35%
2024-07-17 18:00 | 7 | 17 | 18 | 10.32% | 27.62%
2024-07-17 19:00 | 7 | 17 | 19 | 4.723% | 27.78%
2024-07-17 20:00 | 7 | 17 | 20 | 0.8609% | 28.85%
2024-07-17 21:00 | 7 | 17 | 21 | 0% | 30.67%
2024-07-17 22:00 | 7 | 17 | 22 | 0% | 32.34%
2024-07-17 23:00 | 7 | 17 | 23 | 0% | 35.71%
2024-07-18 | 7 | 18 | 0 | 0% | 23.38%
2024-07-18 01:00 | 7 | 18 | 1 | 0% | 29.96%
2024-07-18 02:00 | 7 | 18 | 2 | 0% | 32.18%
2024-07-18 03:00 | 7 | 18 | 3 | 0% | 31.19%
2024-07-18 04:00 | 7 | 18 | 4 | 1.327% | 30.05%
2024-07-18 05:00 | 7 | 18 | 5 | 4.925% | 27.66%
2024-07-18 06:00 | 7 | 18 | 6 | 15.3% | 25.2%
2024-07-18 07:00 | 7 | 18 | 7 | 20.43% | 24.06%
2024-07-18 08:00 | 7 | 18 | 8 | 26% | 25.44%
2024-07-18 09:00 | 7 | 18 | 9 | 37.31% | 23.42%
2024-07-18 10:00 | 7 | 18 | 10 | 58.03% | 23.7%
2024-07-18 11:00 | 7 | 18 | 11 | 46.32% | 24.26%
2024-07-18 12:00 | 7 | 18 | 12 | 39.69% | 25.28%
2024-07-18 13:00 | 7 | 18 | 13 | 75.41% | 26.08%
2024-07-18 14:00 | 7 | 18 | 14 | 36.54% | 26.62%
2024-07-18 15:00 | 7 | 18 | 15 | 35.56% | 26.45%
2024-07-18 16:00 | 7 | 18 | 16 | 23.4% | 25.47%
2024-07-18 17:00 | 7 | 18 | 17 | 16.16% | 23.67%
2024-07-18 18:00 | 7 | 18 | 18 | 8.132% | 22.2%
2024-07-18 19:00 | 7 | 18 | 19 | 4.177% | 21.57%
2024-07-18 20:00 | 7 | 18 | 20 | 1.165% | 21.64%
2024-07-18 21:00 | 7 | 18 | 21 | 0% | 22.68%
2024-07-18 22:00 | 7 | 18 | 22 | 0% | 23.35%
2024-07-18 23:00 | 7 | 18 | 23 | 0% | 23.17%
2024-07-19 | 7 | 19 | 0 | 0% | 15.08%
2024-07-19 01:00 | 7 | 19 | 1 | 0% | 22.69%
2024-07-19 02:00 | 7 | 19 | 2 | 0% | 21.5%
2024-07-19 03:00 | 7 | 19 | 3 | 0% | 20.35%
2024-07-19 04:00 | 7 | 19 | 4 | 1.842% | 18.44%
2024-07-19 05:00 | 7 | 19 | 5 | 4.735% | 15.67%
2024-07-19 06:00 | 7 | 19 | 6 | 17.58% | 13.09%
2024-07-19 07:00 | 7 | 19 | 7 | 32.39% | 11.52%
2024-07-19 08:00 | 7 | 19 | 8 | 40.69% | 12.68%
2024-07-19 09:00 | 7 | 19 | 9 | 63.63% | 10.76%
2024-07-19 10:00 | 7 | 19 | 10 | 73.55% | 10.92%
2024-07-19 11:00 | 7 | 19 | 11 | 75.41% | 11.38%
2024-07-19 12:00 | 7 | 19 | 12 | 75.41% | 11.57%
2024-07-19 13:00 | 7 | 19 | 13 | 75.41% | 11.55%
2024-07-19 14:00 | 7 | 19 | 14 | 75.41% | 12.31%
2024-07-19 15:00 | 7 | 19 | 15 | 63.63% | 12.27%
2024-07-19 16:00 | 7 | 19 | 16 | 46.4% | 11.12%
2024-07-19 17:00 | 7 | 19 | 17 | 26.72% | 10.48%
2024-07-19 18:00 | 7 | 19 | 18 | 9.172% | 10.05%
2024-07-19 19:00 | 7 | 19 | 19 | 4.087% | 10.37%
2024-07-19 20:00 | 7 | 19 | 20 | 1.289% | 10.89%
2024-07-19 21:00 | 7 | 19 | 21 | 0% | 12.61%
2024-07-19 22:00 | 7 | 19 | 22 | 0% | 14.06%
2024-07-19 23:00 | 7 | 19 | 23 | 0% | 14.57%
2024-07-20 | 7 | 20 | 0 | 0% | 21.31%
2024-07-20 01:00 | 7 | 20 | 1 | 0% | 15.83%
2024-07-20 02:00 | 7 | 20 | 2 | 0% | 14.35%
2024-07-20 03:00 | 7 | 20 | 3 | 0% | 13.36%
2024-07-20 04:00 | 7 | 20 | 4 | 3.64% | 12.34%
2024-07-20 05:00 | 7 | 20 | 5 | 4.355% | 10.64%
2024-07-20 06:00 | 7 | 20 | 6 | 17.79% | 8.912%
2024-07-20 07:00 | 7 | 20 | 7 | 38.11% | 7.505%
2024-07-20 08:00 | 7 | 20 | 8 | 56.54% | 7.613%
2024-07-20 09:00 | 7 | 20 | 9 | 71.01% | 6.983%
2024-07-20 10:00 | 7 | 20 | 10 | 75.41% | 7.521%
2024-07-20 11:00 | 7 | 20 | 11 | 75.41% | 8.301%
2024-07-20 12:00 | 7 | 20 | 12 | 75.41% | 9.381%
2024-07-20 13:00 | 7 | 20 | 13 | 75.41% | 10.42%
2024-07-20 14:00 | 7 | 20 | 14 | 75.41% | 11.27%
2024-07-20 15:00 | 7 | 20 | 15 | 63.68% | 12.06%
2024-07-20 16:00 | 7 | 20 | 16 | 46.69% | 12.65%
2024-07-20 17:00 | 7 | 20 | 17 | 21.94% | 13.61%
2024-07-20 18:00 | 7 | 20 | 18 | 9.723% | 12.79%
2024-07-20 19:00 | 7 | 20 | 19 | 4.347% | 14.04%
2024-07-20 20:00 | 7 | 20 | 20 | 0% | 16.34%
2024-07-20 21:00 | 7 | 20 | 21 | 0% | 19.02%
2024-07-20 22:00 | 7 | 20 | 22 | 0% | 21%
2024-07-20 23:00 | 7 | 20 | 23 | 0% | 21.46%
2024-07-21 | 7 | 21 | 0 | 0% | 22.11%
2024-07-21 01:00 | 7 | 21 | 1 | 0% | 21.06%
2024-07-21 02:00 | 7 | 21 | 2 | 0% | 20.27%
2024-07-21 03:00 | 7 | 21 | 3 | 0% | 20.04%
2024-07-21 04:00 | 7 | 21 | 4 | 0.1719% | 19.06%
2024-07-21 05:00 | 7 | 21 | 5 | 1.387% | 17.01%
2024-07-21 06:00 | 7 | 21 | 6 | 2.962% | 14.29%
2024-07-21 07:00 | 7 | 21 | 7 | 5.879% | 12.06%
2024-07-21 08:00 | 7 | 21 | 8 | 5.95% | 11.17%
2024-07-21 09:00 | 7 | 21 | 9 | 11.42% | 11.06%
2024-07-21 10:00 | 7 | 21 | 10 | 32.3% | 11.62%
2024-07-21 11:00 | 7 | 21 | 11 | 16.94% | 12.7%
2024-07-21 12:00 | 7 | 21 | 12 | 11.88% | 13.5%
2024-07-21 13:00 | 7 | 21 | 13 | 11.48% | 14.3%
2024-07-21 14:00 | 7 | 21 | 14 | 15.55% | 14.87%
2024-07-21 15:00 | 7 | 21 | 15 | 13.53% | 15.22%
2024-07-21 16:00 | 7 | 21 | 16 | 9.926% | 15.33%
2024-07-21 17:00 | 7 | 21 | 17 | 9.064% | 15.01%
2024-07-21 18:00 | 7 | 21 | 18 | 9.382% | 15.1%
2024-07-21 19:00 | 7 | 21 | 19 | 3.439% | 15.68%
2024-07-21 20:00 | 7 | 21 | 20 | 0.2353% | 16.89%
2024-07-21 21:00 | 7 | 21 | 21 | 0% | 18.85%
2024-07-21 22:00 | 7 | 21 | 22 | 0% | 20.32%
2024-07-21 23:00 | 7 | 21 | 23 | 0% | 21.67%
2024-07-22 | 7 | 22 | 0 | 0% | 21.28%
2024-07-22 01:00 | 7 | 22 | 1 | 0% | 22.16%
2024-07-22 02:00 | 7 | 22 | 2 | 0% | 21.52%
2024-07-22 03:00 | 7 | 22 | 3 | 0% | 21.07%
2024-07-22 04:00 | 7 | 22 | 4 | 0.5199% | 20.23%
2024-07-22 05:00 | 7 | 22 | 5 | 5.463% | 18.24%
2024-07-22 06:00 | 7 | 22 | 6 | 13.41% | 16.48%
2024-07-22 07:00 | 7 | 22 | 7 | 28.21% | 15.47%
2024-07-22 08:00 | 7 | 22 | 8 | 42.47% | 15.38%
2024-07-22 09:00 | 7 | 22 | 9 | 63.58% | 16.63%
2024-07-22 10:00 | 7 | 22 | 10 | 75.13% | 18.1%
2024-07-22 11:00 | 7 | 22 | 11 | 61.59% | 19.07%
2024-07-22 12:00 | 7 | 22 | 12 | 63.99% | 20.05%
2024-07-22 13:00 | 7 | 22 | 13 | 35.05% | 20.74%
2024-07-22 14:00 | 7 | 22 | 14 | 66.42% | 21.13%
2024-07-22 15:00 | 7 | 22 | 15 | 56.34% | 21.25%
2024-07-22 16:00 | 7 | 22 | 16 | 23.55% | 21.08%
2024-07-22 17:00 | 7 | 22 | 17 | 12.39% | 20.16%
2024-07-22 18:00 | 7 | 22 | 18 | 5.27% | 19.25%
2024-07-22 19:00 | 7 | 22 | 19 | 2.552% | 18.56%
2024-07-22 20:00 | 7 | 22 | 20 | 0% | 19.19%
2024-07-22 21:00 | 7 | 22 | 21 | 0% | 20.02%
2024-07-22 22:00 | 7 | 22 | 22 | 0% | 20.41%
2024-07-22 23:00 | 7 | 22 | 23 | 0% | 22.68%
2024-07-23 | 7 | 23 | 0 | 0% | 13.79%
2024-07-23 01:00 | 7 | 23 | 1 | 0% | 19.08%
2024-07-23 02:00 | 7 | 23 | 2 | 0% | 18.36%
2024-07-23 03:00 | 7 | 23 | 3 | 0% | 17.37%
2024-07-23 04:00 | 7 | 23 | 4 | 1.079% | 16.07%
2024-07-23 05:00 | 7 | 23 | 5 | 4.133% | 14.66%
2024-07-23 06:00 | 7 | 23 | 6 | 14.87% | 12.74%
2024-07-23 07:00 | 7 | 23 | 7 | 13.97% | 11.79%
2024-07-23 08:00 | 7 | 23 | 8 | 25.23% | 11.32%
2024-07-23 09:00 | 7 | 23 | 9 | 20.96% | 11.56%
2024-07-23 10:00 | 7 | 23 | 10 | 23.28% | 12.39%
2024-07-23 11:00 | 7 | 23 | 11 | 21.74% | 13.14%
2024-07-23 12:00 | 7 | 23 | 12 | 20.12% | 13.71%
2024-07-23 13:00 | 7 | 23 | 13 | 17.34% | 14.14%
2024-07-23 14:00 | 7 | 23 | 14 | 17.7% | 14.19%
2024-07-23 15:00 | 7 | 23 | 15 | 10.57% | 14.96%
2024-07-23 16:00 | 7 | 23 | 16 | 5.881% | 13.51%
2024-07-23 17:00 | 7 | 23 | 17 | 4.126% | 12.87%
2024-07-23 18:00 | 7 | 23 | 18 | 4.121% | 11.91%
2024-07-23 19:00 | 7 | 23 | 19 | 1.998% | 11.58%
2024-07-23 20:00 | 7 | 23 | 20 | 0% | 12.17%
2024-07-23 21:00 | 7 | 23 | 21 | 0% | 13.03%
2024-07-23 22:00 | 7 | 23 | 22 | 0% | 13.72%
2024-07-23 23:00 | 7 | 23 | 23 | 0% | 13.78%
2024-07-24 | 7 | 24 | 0 | 0% | 14.94%
2024-07-24 01:00 | 7 | 24 | 1 | 0% | 13.71%
2024-07-24 02:00 | 7 | 24 | 2 | 0% | 13.51%
2024-07-24 03:00 | 7 | 24 | 3 | 0% | 13.33%
2024-07-24 04:00 | 7 | 24 | 4 | 0% | 12.72%
2024-07-24 05:00 | 7 | 24 | 5 | 3.439% | 11.33%
2024-07-24 06:00 | 7 | 24 | 6 | 4.715% | 9.893%
2024-07-24 07:00 | 7 | 24 | 7 | 8.865% | 9.418%
2024-07-24 08:00 | 7 | 24 | 8 | 11.84% | 10.37%
2024-07-24 09:00 | 7 | 24 | 9 | 16.05% | 10.57%
2024-07-24 10:00 | 7 | 24 | 10 | 14.02% | 10.33%
2024-07-24 11:00 | 7 | 24 | 11 | 16.48% | 10.83%
2024-07-24 12:00 | 7 | 24 | 12 | 16.82% | 12.15%
2024-07-24 13:00 | 7 | 24 | 13 | 13.95% | 11.56%
2024-07-24 14:00 | 7 | 24 | 14 | 14.73% | 11.96%
2024-07-24 15:00 | 7 | 24 | 15 | 25.29% | 12%
2024-07-24 16:00 | 7 | 24 | 16 | 14.61% | 12.06%
2024-07-24 17:00 | 7 | 24 | 17 | 5.744% | 11.92%
2024-07-24 18:00 | 7 | 24 | 18 | 3.117% | 11.62%
2024-07-24 19:00 | 7 | 24 | 19 | 1.999% | 11.62%
2024-07-24 20:00 | 7 | 24 | 20 | 0% | 12.81%
2024-07-24 21:00 | 7 | 24 | 21 | 0% | 14.12%
2024-07-24 22:00 | 7 | 24 | 22 | 0% | 14.91%
2024-07-24 23:00 | 7 | 24 | 23 | 0% | 15.94%
2024-07-25 | 7 | 25 | 0 | 0% | 21.69%
2024-07-25 01:00 | 7 | 25 | 1 | 0% | 14.26%
2024-07-25 02:00 | 7 | 25 | 2 | 0% | 13.58%
2024-07-25 03:00 | 7 | 25 | 3 | 0% | 12.59%
2024-07-25 04:00 | 7 | 25 | 4 | 0.783% | 11.67%
2024-07-25 05:00 | 7 | 25 | 5 | 2.268% | 10.47%
2024-07-25 06:00 | 7 | 25 | 6 | 8.419% | 9.379%
2024-07-25 07:00 | 7 | 25 | 7 | 15.25% | 9.081%
2024-07-25 08:00 | 7 | 25 | 8 | 25.72% | 9.642%
2024-07-25 09:00 | 7 | 25 | 9 | 51.43% | 10.76%
2024-07-25 10:00 | 7 | 25 | 10 | 65.56% | 12.31%
2024-07-25 11:00 | 7 | 25 | 11 | 46.19% | 14.08%
2024-07-25 12:00 | 7 | 25 | 12 | 51.53% | 15.83%
2024-07-25 13:00 | 7 | 25 | 13 | 45.2% | 17.32%
2024-07-25 14:00 | 7 | 25 | 14 | 30.19% | 18.21%
2024-07-25 15:00 | 7 | 25 | 15 | 16.46% | 18.67%
2024-07-25 16:00 | 7 | 25 | 16 | 13.33% | 18.66%
2024-07-25 17:00 | 7 | 25 | 17 | 7.84% | 18.51%
2024-07-25 18:00 | 7 | 25 | 18 | 4.983% | 17.96%
2024-07-25 19:00 | 7 | 25 | 19 | 2.155% | 18.09%
2024-07-25 20:00 | 7 | 25 | 20 | 0% | 18.96%
2024-07-25 21:00 | 7 | 25 | 21 | 0% | 20.29%
2024-07-25 22:00 | 7 | 25 | 22 | 0% | 23.18%
2024-07-25 23:00 | 7 | 25 | 23 | 0% | 21.53%
2024-07-26 | 7 | 26 | 0 | 0% | 25.59%
2024-07-26 01:00 | 7 | 26 | 1 | 0% | 21.24%
2024-07-26 02:00 | 7 | 26 | 2 | 0% | 20.3%
2024-07-26 03:00 | 7 | 26 | 3 | 0% | 19.48%
2024-07-26 04:00 | 7 | 26 | 4 | 0.7778% | 18.72%
2024-07-26 05:00 | 7 | 26 | 5 | 4.419% | 17.38%
2024-07-26 06:00 | 7 | 26 | 6 | 15.7% | 16.31%
2024-07-26 07:00 | 7 | 26 | 7 | 35.16% | 17.38%
2024-07-26 08:00 | 7 | 26 | 8 | 53.63% | 16.64%
2024-07-26 09:00 | 7 | 26 | 9 | 54.28% | 17.73%
2024-07-26 10:00 | 7 | 26 | 10 | 54.2% | 19.09%
2024-07-26 11:00 | 7 | 26 | 11 | 36.04% | 20.97%
2024-07-26 12:00 | 7 | 26 | 12 | 38.11% | 25.11%
2024-07-26 13:00 | 7 | 26 | 13 | 49.39% | 25.05%
2024-07-26 14:00 | 7 | 26 | 14 | 35.47% | 26.17%
2024-07-26 15:00 | 7 | 26 | 15 | 38.8% | 27.25%
2024-07-26 16:00 | 7 | 26 | 16 | 42.25% | 27.57%
2024-07-26 17:00 | 7 | 26 | 17 | 20.07% | 26.84%
2024-07-26 18:00 | 7 | 26 | 18 | 9.216% | 25.7%
2024-07-26 19:00 | 7 | 26 | 19 | 3.603% | 25.29%
2024-07-26 20:00 | 7 | 26 | 20 | 0% | 25.89%
2024-07-26 21:00 | 7 | 26 | 21 | 0% | 26.92%
2024-07-26 22:00 | 7 | 26 | 22 | 0% | 26.9%
2024-07-26 23:00 | 7 | 26 | 23 | 0% | 26.4%
2024-07-27 | 7 | 27 | 0 | 0% | 19.03%
2024-07-27 01:00 | 7 | 27 | 1 | 0% | 26.59%
2024-07-27 02:00 | 7 | 27 | 2 | 0% | 24.01%
2024-07-27 03:00 | 7 | 27 | 3 | 0% | 23.12%
2024-07-27 04:00 | 7 | 27 | 4 | 1.502% | 21.61%
2024-07-27 05:00 | 7 | 27 | 5 | 3.977% | 19.65%
2024-07-27 06:00 | 7 | 27 | 6 | 15.59% | 17.63%
2024-07-27 07:00 | 7 | 27 | 7 | 26.13% | 16.67%
2024-07-27 08:00 | 7 | 27 | 8 | 20.89% | 16.41%
2024-07-27 09:00 | 7 | 27 | 9 | 27.27% | 16.91%
2024-07-27 10:00 | 7 | 27 | 10 | 32.8% | 17.34%
2024-07-27 11:00 | 7 | 27 | 11 | 18.26% | 18.09%
2024-07-27 12:00 | 7 | 27 | 12 | 23.13% | 17.96%
2024-07-27 13:00 | 7 | 27 | 13 | 20.2% | 17.66%
2024-07-27 14:00 | 7 | 27 | 14 | 16.14% | 17.24%
2024-07-27 15:00 | 7 | 27 | 15 | 10.02% | 16.8%
2024-07-27 16:00 | 7 | 27 | 16 | 5.584% | 16.5%
2024-07-27 17:00 | 7 | 27 | 17 | 5.01% | 16.39%
2024-07-27 18:00 | 7 | 27 | 18 | 4.383% | 14.95%
2024-07-27 19:00 | 7 | 27 | 19 | 1.582% | 15.19%
2024-07-27 20:00 | 7 | 27 | 20 | 0% | 16.68%
2024-07-27 21:00 | 7 | 27 | 21 | 0% | 18.23%
2024-07-27 22:00 | 7 | 27 | 22 | 0% | 18.9%
2024-07-27 23:00 | 7 | 27 | 23 | 0% | 18.98%
2024-07-28 | 7 | 28 | 0 | 0% | 22.23%
2024-07-28 01:00 | 7 | 28 | 1 | 0% | 18.83%
2024-07-28 02:00 | 7 | 28 | 2 | 0% | 18.56%
2024-07-28 03:00 | 7 | 28 | 3 | 0% | 18.38%
2024-07-28 04:00 | 7 | 28 | 4 | 0.9633% | 17.91%
2024-07-28 05:00 | 7 | 28 | 5 | 4.707% | 16.32%
2024-07-28 06:00 | 7 | 28 | 6 | 15% | 14.52%
2024-07-28 07:00 | 7 | 28 | 7 | 24.64% | 13.59%
2024-07-28 08:00 | 7 | 28 | 8 | 51.17% | 13.83%
2024-07-28 09:00 | 7 | 28 | 9 | 70.12% | 14.11%
2024-07-28 10:00 | 7 | 28 | 10 | 75.41% | 15.98%
2024-07-28 11:00 | 7 | 28 | 11 | 75.41% | 16.26%
2024-07-28 12:00 | 7 | 28 | 12 | 75.41% | 17.06%
2024-07-28 13:00 | 7 | 28 | 13 | 75.41% | 17.76%
2024-07-28 14:00 | 7 | 28 | 14 | 75.02% | 18.53%
2024-07-28 15:00 | 7 | 28 | 15 | 62.22% | 18.56%
2024-07-28 16:00 | 7 | 28 | 16 | 44.6% | 18.55%
2024-07-28 17:00 | 7 | 28 | 17 | 23.54% | 17.76%
2024-07-28 18:00 | 7 | 28 | 18 | 8.079% | 16.9%
2024-07-28 19:00 | 7 | 28 | 19 | 3.388% | 16.88%
2024-07-28 20:00 | 7 | 28 | 20 | 0% | 18.98%
2024-07-28 21:00 | 7 | 28 | 21 | 0% | 19.82%
2024-07-28 22:00 | 7 | 28 | 22 | 0% | 21.42%
2024-07-28 23:00 | 7 | 28 | 23 | 0% | 22.02%
2024-07-29 | 7 | 29 | 0 | 0% | 20.22%
2024-07-29 01:00 | 7 | 29 | 1 | 0% | 22.05%
2024-07-29 02:00 | 7 | 29 | 2 | 0% | 21.77%
2024-07-29 03:00 | 7 | 29 | 3 | 0% | 21.58%
2024-07-29 04:00 | 7 | 29 | 4 | 0.7829% | 21.33%
2024-07-29 05:00 | 7 | 29 | 5 | 4.048% | 19.72%
2024-07-29 06:00 | 7 | 29 | 6 | 14.22% | 17.91%
2024-07-29 07:00 | 7 | 29 | 7 | 12.53% | 16.7%
2024-07-29 08:00 | 7 | 29 | 8 | 9.743% | 16.23%
2024-07-29 09:00 | 7 | 29 | 9 | 13.36% | 16.72%
2024-07-29 10:00 | 7 | 29 | 10 | 13.11% | 17.67%
2024-07-29 11:00 | 7 | 29 | 11 | 13.41% | 18.75%
2024-07-29 12:00 | 7 | 29 | 12 | 11.83% | 21.02%
2024-07-29 13:00 | 7 | 29 | 13 | 19.37% | 19.76%
2024-07-29 14:00 | 7 | 29 | 14 | 11.07% | 19.96%
2024-07-29 15:00 | 7 | 29 | 15 | 11.48% | 20.94%
2024-07-29 16:00 | 7 | 29 | 16 | 11.17% | 19.02%
2024-07-29 17:00 | 7 | 29 | 17 | 15.76% | 18.05%
2024-07-29 18:00 | 7 | 29 | 18 | 7.61% | 14.98%
2024-07-29 19:00 | 7 | 29 | 19 | 2.771% | 17.42%
2024-07-29 20:00 | 7 | 29 | 20 | 0% | 18.04%
2024-07-29 21:00 | 7 | 29 | 21 | 0% | 18.93%
2024-07-29 22:00 | 7 | 29 | 22 | 0% | 19.96%
2024-07-29 23:00 | 7 | 29 | 23 | 0% | 20.46%
2024-07-30 | 7 | 30 | 0 | 0% | 24.85%
2024-07-30 01:00 | 7 | 30 | 1 | 0% | 19.83%
2024-07-30 02:00 | 7 | 30 | 2 | 0% | 19.5%
2024-07-30 03:00 | 7 | 30 | 3 | 0% | 19.29%
2024-07-30 04:00 | 7 | 30 | 4 | 0.4274% | 18.85%
2024-07-30 05:00 | 7 | 30 | 5 | 5.015% | 17.52%
2024-07-30 06:00 | 7 | 30 | 6 | 10.86% | 16.01%
2024-07-30 07:00 | 7 | 30 | 7 | 23.94% | 15.15%
2024-07-30 08:00 | 7 | 30 | 8 | 24.25% | 15%
2024-07-30 09:00 | 7 | 30 | 9 | 24.25% | 15.82%
2024-07-30 10:00 | 7 | 30 | 10 | 43.18% | 16.66%
2024-07-30 11:00 | 7 | 30 | 11 | 20.89% | 17.62%
2024-07-30 12:00 | 7 | 30 | 12 | 12.77% | 19.07%
2024-07-30 13:00 | 7 | 30 | 13 | 9.871% | 20.27%
2024-07-30 14:00 | 7 | 30 | 14 | 11.19% | 21.1%
2024-07-30 15:00 | 7 | 30 | 15 | 14.52% | 22.07%
2024-07-30 16:00 | 7 | 30 | 16 | 12.03% | 21.92%
2024-07-30 17:00 | 7 | 30 | 17 | 9.366% | 20.97%
2024-07-30 18:00 | 7 | 30 | 18 | 7.696% | 20.06%
2024-07-30 19:00 | 7 | 30 | 19 | 3.153% | 20.11%
2024-07-30 20:00 | 7 | 30 | 20 | 0% | 21.77%
2024-07-30 21:00 | 7 | 30 | 21 | 0% | 23.56%
2024-07-30 22:00 | 7 | 30 | 22 | 0% | 24.51%
2024-07-30 23:00 | 7 | 30 | 23 | 0% | 25.08%
2024-07-31 | 7 | 31 | 0 | 0% | 17.21%
2024-07-31 01:00 | 7 | 31 | 1 | 0% | 24.6%
2024-07-31 02:00 | 7 | 31 | 2 | 0% | 24.1%
2024-07-31 03:00 | 7 | 31 | 3 | 0% | 23.16%
2024-07-31 04:00 | 7 | 31 | 4 | 1.123% | 22.15%
2024-07-31 05:00 | 7 | 31 | 5 | 3.288% | 20.24%
2024-07-31 06:00 | 7 | 31 | 6 | 12.6% | 18.82%
2024-07-31 07:00 | 7 | 31 | 7 | 26.05% | 17.95%
2024-07-31 08:00 | 7 | 31 | 8 | 43.62% | 18.08%
2024-07-31 09:00 | 7 | 31 | 9 | 58.77% | 18.01%
2024-07-31 10:00 | 7 | 31 | 10 | 70.27% | 18.02%
2024-07-31 11:00 | 7 | 31 | 11 | 69.29% | 18.39%
2024-07-31 12:00 | 7 | 31 | 12 | 75.27% | 18.12%
2024-07-31 13:00 | 7 | 31 | 13 | 75.41% | 17.89%
2024-07-31 14:00 | 7 | 31 | 14 | 67.83% | 18.01%
2024-07-31 15:00 | 7 | 31 | 15 | 40.47% | 15.32%
2024-07-31 16:00 | 7 | 31 | 16 | 36.1% | 16.83%
2024-07-31 17:00 | 7 | 31 | 17 | 10.88% | 15.81%
2024-07-31 18:00 | 7 | 31 | 18 | 6.729% | 14.95%
2024-07-31 19:00 | 7 | 31 | 19 | 3.032% | 14.61%
2024-07-31 20:00 | 7 | 31 | 20 | 0% | 15.1%
2024-07-31 21:00 | 7 | 31 | 21 | 0% | 15.86%
2024-07-31 22:00 | 7 | 31 | 22 | 0% | 16.53%
2024-07-31 23:00 | 7 | 31 | 23 | 0% | 16.46%
2024-08-01 | 8 | 1 | 0 | 0% | 15.46%
2024-08-01 01:00 | 8 | 1 | 1 | 0% | 15.62%
2024-08-01 02:00 | 8 | 1 | 2 | 0% | 15.04%
2024-08-01 03:00 | 8 | 1 | 3 | 0% | 14.54%
2024-08-01 04:00 | 8 | 1 | 4 | 0.9508% | 14.02%
2024-08-01 05:00 | 8 | 1 | 5 | 3.541% | 10.87%
2024-08-01 06:00 | 8 | 1 | 6 | 9.052% | 11.06%
2024-08-01 07:00 | 8 | 1 | 7 | 14.71% | 10.47%
2024-08-01 08:00 | 8 | 1 | 8 | 30.36% | 10.47%
2024-08-01 09:00 | 8 | 1 | 9 | 42.06% | 10.61%
2024-08-01 10:00 | 8 | 1 | 10 | 50.05% | 11.28%
2024-08-01 11:00 | 8 | 1 | 11 | 50.14% | 12.03%
2024-08-01 12:00 | 8 | 1 | 12 | 72.63% | 14.1%
2024-08-01 13:00 | 8 | 1 | 13 | 70.44% | 13.49%
2024-08-01 14:00 | 8 | 1 | 14 | 72.42% | 13.47%
2024-08-01 15:00 | 8 | 1 | 15 | 54.91% | 13.65%
2024-08-01 16:00 | 8 | 1 | 16 | 27.25% | 13.37%
2024-08-01 17:00 | 8 | 1 | 17 | 19.86% | 12.24%
2024-08-01 18:00 | 8 | 1 | 18 | 7.341% | 11.44%
2024-08-01 19:00 | 8 | 1 | 19 | 2.122% | 11.51%
2024-08-01 20:00 | 8 | 1 | 20 | 0% | 12.8%
2024-08-01 21:00 | 8 | 1 | 21 | 0% | 13.83%
2024-08-01 22:00 | 8 | 1 | 22 | 0% | 14.65%
2024-08-01 23:00 | 8 | 1 | 23 | 0% | 15.1%
2024-08-02 | 8 | 2 | 0 | 0% | 22.48%
2024-08-02 01:00 | 8 | 2 | 1 | 0% | 15.57%
2024-08-02 02:00 | 8 | 2 | 2 | 0% | 15.69%
2024-08-02 03:00 | 8 | 2 | 3 | 0% | 15.8%
2024-08-02 04:00 | 8 | 2 | 4 | 0% | 15.54%
2024-08-02 05:00 | 8 | 2 | 5 | 2.558% | 13.8%
2024-08-02 06:00 | 8 | 2 | 6 | 8.396% | 12.42%
2024-08-02 07:00 | 8 | 2 | 7 | 22.67% | 11.62%
2024-08-02 08:00 | 8 | 2 | 8 | 37.08% | 12.1%
2024-08-02 09:00 | 8 | 2 | 9 | 44.58% | 12.7%
2024-08-02 10:00 | 8 | 2 | 10 | 42.16% | 13.95%
2024-08-02 11:00 | 8 | 2 | 11 | 31.62% | 15.32%
2024-08-02 12:00 | 8 | 2 | 12 | 57.33% | 16.58%
2024-08-02 13:00 | 8 | 2 | 13 | 69.88% | 18.4%
2024-08-02 14:00 | 8 | 2 | 14 | 52.74% | 19.12%
2024-08-02 15:00 | 8 | 2 | 15 | 31.9% | 19.59%
2024-08-02 16:00 | 8 | 2 | 16 | 15.88% | 19.49%
2024-08-02 17:00 | 8 | 2 | 17 | 12.43% | 19.02%
2024-08-02 18:00 | 8 | 2 | 18 | 4.092% | 18.35%
2024-08-02 19:00 | 8 | 2 | 19 | 2.034% | 18.51%
2024-08-02 20:00 | 8 | 2 | 20 | 0% | 20.02%
2024-08-02 21:00 | 8 | 2 | 21 | 0% | 21.77%
2024-08-02 22:00 | 8 | 2 | 22 | 0% | 22.49%
2024-08-02 23:00 | 8 | 2 | 23 | 0% | 22.5%
2024-08-03 | 8 | 3 | 0 | 0% | 20.5%
2024-08-03 01:00 | 8 | 3 | 1 | 0% | 21.85%
2024-08-03 02:00 | 8 | 3 | 2 | 0% | 20.92%
2024-08-03 03:00 | 8 | 3 | 3 | 0% | 20.41%
2024-08-03 04:00 | 8 | 3 | 4 | 0% | 18.97%
2024-08-03 05:00 | 8 | 3 | 5 | 1.288% | 16.83%
2024-08-03 06:00 | 8 | 3 | 6 | 7.887% | 14.55%
2024-08-03 07:00 | 8 | 3 | 7 | 10.62% | 13.36%
2024-08-03 08:00 | 8 | 3 | 8 | 27.47% | 13%
2024-08-03 09:00 | 8 | 3 | 9 | 62.71% | 13.41%
2024-08-03 10:00 | 8 | 3 | 10 | 75.41% | 14.44%
2024-08-03 11:00 | 8 | 3 | 11 | 75.41% | 15.55%
2024-08-03 12:00 | 8 | 3 | 12 | 75.41% | 16.84%
2024-08-03 13:00 | 8 | 3 | 13 | 71.66% | 17.71%
2024-08-03 14:00 | 8 | 3 | 14 | 55.72% | 20.1%
2024-08-03 15:00 | 8 | 3 | 15 | 57.61% | 19.14%
2024-08-03 16:00 | 8 | 3 | 16 | 42.73% | 19.11%
2024-08-03 17:00 | 8 | 3 | 17 | 22.65% | 18.48%
2024-08-03 18:00 | 8 | 3 | 18 | 7.288% | 18.4%
2024-08-03 19:00 | 8 | 3 | 19 | 3.079% | 18.87%
2024-08-03 20:00 | 8 | 3 | 20 | 0% | 20.3%
2024-08-03 21:00 | 8 | 3 | 21 | 0% | 21.26%
2024-08-03 22:00 | 8 | 3 | 22 | 0% | 21.48%
2024-08-03 23:00 | 8 | 3 | 23 | 0% | 21.13%
2024-08-04 | 8 | 4 | 0 | 0% | 22.38%
2024-08-04 01:00 | 8 | 4 | 1 | 0% | 19.67%
2024-08-04 02:00 | 8 | 4 | 2 | 0% | 18.91%
2024-08-04 03:00 | 8 | 4 | 3 | 0% | 17.97%
2024-08-04 04:00 | 8 | 4 | 4 | 0.9825% | 17.25%
2024-08-04 05:00 | 8 | 4 | 5 | 4.489% | 15.91%
2024-08-04 06:00 | 8 | 4 | 6 | 13.85% | 14.68%
2024-08-04 07:00 | 8 | 4 | 7 | 30.9% | 13.54%
2024-08-04 08:00 | 8 | 4 | 8 | 53.89% | 13.45%
2024-08-04 09:00 | 8 | 4 | 9 | 68.37% | 13.7%
2024-08-04 10:00 | 8 | 4 | 10 | 75.41% | 13.98%
2024-08-04 11:00 | 8 | 4 | 11 | 56.17% | 14.15%
2024-08-04 12:00 | 8 | 4 | 12 | 75.41% | 14.66%
2024-08-04 13:00 | 8 | 4 | 13 | 75.41% | 15.27%
2024-08-04 14:00 | 8 | 4 | 14 | 72.71% | 15.8%
2024-08-04 15:00 | 8 | 4 | 15 | 59.38% | 16.61%
2024-08-04 16:00 | 8 | 4 | 16 | 41.62% | 16.83%
2024-08-04 17:00 | 8 | 4 | 17 | 21.41% | 17.27%
2024-08-04 18:00 | 8 | 4 | 18 | 7.601% | 17.4%
2024-08-04 19:00 | 8 | 4 | 19 | 2.107% | 18.49%
2024-08-04 20:00 | 8 | 4 | 20 | 0% | 20.09%
2024-08-04 21:00 | 8 | 4 | 21 | 0% | 21.7%
2024-08-04 22:00 | 8 | 4 | 22 | 0% | 22.54%
2024-08-04 23:00 | 8 | 4 | 23 | 0% | 23.14%
2024-08-05 | 8 | 5 | 0 | 0% | 25.27%
2024-08-05 01:00 | 8 | 5 | 1 | 0% | 21.56%
2024-08-05 02:00 | 8 | 5 | 2 | 0% | 20.68%
2024-08-05 03:00 | 8 | 5 | 3 | 0% | 19.39%
2024-08-05 04:00 | 8 | 5 | 4 | 0% | 18.43%
2024-08-05 05:00 | 8 | 5 | 5 | 0.8365% | 18.09%
2024-08-05 06:00 | 8 | 5 | 6 | 5.386% | 17.33%
2024-08-05 07:00 | 8 | 5 | 7 | 9.582% | 17.23%
2024-08-05 08:00 | 8 | 5 | 8 | 14.75% | 17.82%
2024-08-05 09:00 | 8 | 5 | 9 | 21.56% | 18.69%
2024-08-05 10:00 | 8 | 5 | 10 | 26.41% | 19.76%
2024-08-05 11:00 | 8 | 5 | 11 | 25.99% | 21.24%
2024-08-05 12:00 | 8 | 5 | 12 | 37.42% | 22.42%
2024-08-05 13:00 | 8 | 5 | 13 | 49.78% | 23.49%
2024-08-05 14:00 | 8 | 5 | 14 | 72.89% | 24.76%
2024-08-05 15:00 | 8 | 5 | 15 | 60.41% | 24.94%
2024-08-05 16:00 | 8 | 5 | 16 | 42.71% | 25.73%
2024-08-05 17:00 | 8 | 5 | 17 | 22.56% | 25.53%
2024-08-05 18:00 | 8 | 5 | 18 | 6.424% | 25.18%
2024-08-05 19:00 | 8 | 5 | 19 | 2.87% | 25.31%
2024-08-05 20:00 | 8 | 5 | 20 | 0% | 25.84%
2024-08-05 21:00 | 8 | 5 | 21 | 0% | 26.79%
2024-08-05 22:00 | 8 | 5 | 22 | 0% | 26.73%
2024-08-05 23:00 | 8 | 5 | 23 | 0% | 25.75%
2024-08-06 | 8 | 6 | 0 | 0% | 29.57%
2024-08-06 01:00 | 8 | 6 | 1 | 0% | 24.43%
2024-08-06 02:00 | 8 | 6 | 2 | 0% | 23.96%
2024-08-06 03:00 | 8 | 6 | 3 | 0% | 23.65%
2024-08-06 04:00 | 8 | 6 | 4 | 0% | 23.35%
2024-08-06 05:00 | 8 | 6 | 5 | 4.147% | 24.64%
2024-08-06 06:00 | 8 | 6 | 6 | 12.59% | 23.39%
2024-08-06 07:00 | 8 | 6 | 7 | 31.45% | 23.06%
2024-08-06 08:00 | 8 | 6 | 8 | 50.05% | 23.69%
2024-08-06 09:00 | 8 | 6 | 9 | 64.97% | 24.33%
2024-08-06 10:00 | 8 | 6 | 10 | 75.41% | 24.17%
2024-08-06 11:00 | 8 | 6 | 11 | 75.41% | 25.43%
2024-08-06 12:00 | 8 | 6 | 12 | 75.41% | 25.71%
2024-08-06 13:00 | 8 | 6 | 13 | 75.41% | 25.77%
2024-08-06 14:00 | 8 | 6 | 14 | 71.56% | 25.54%
2024-08-06 15:00 | 8 | 6 | 15 | 58.81% | 25.76%
2024-08-06 16:00 | 8 | 6 | 16 | 41.33% | 26.44%
2024-08-06 17:00 | 8 | 6 | 17 | 21.65% | 26.64%
2024-08-06 18:00 | 8 | 6 | 18 | 6.31% | 26.63%
2024-08-06 19:00 | 8 | 6 | 19 | 2.538% | 26.92%
2024-08-06 20:00 | 8 | 6 | 20 | 0% | 28.22%
2024-08-06 21:00 | 8 | 6 | 21 | 0% | 29.19%
2024-08-06 22:00 | 8 | 6 | 22 | 0% | 29.66%
2024-08-06 23:00 | 8 | 6 | 23 | 0% | 30.35%
2024-08-07 | 8 | 7 | 0 | 0% | 23.23%
2024-08-07 01:00 | 8 | 7 | 1 | 0% | 29.76%
2024-08-07 02:00 | 8 | 7 | 2 | 0% | 28.84%
2024-08-07 03:00 | 8 | 7 | 3 | 0% | 27.96%
2024-08-07 04:00 | 8 | 7 | 4 | 0% | 27.26%
2024-08-07 05:00 | 8 | 7 | 5 | 3.143% | 25.25%
2024-08-07 06:00 | 8 | 7 | 6 | 10.59% | 23.12%
2024-08-07 07:00 | 8 | 7 | 7 | 29.45% | 20.99%
2024-08-07 08:00 | 8 | 7 | 8 | 49.58% | 20.54%
2024-08-07 09:00 | 8 | 7 | 9 | 64.64% | 20.68%
2024-08-07 10:00 | 8 | 7 | 10 | 75.14% | 21.61%
2024-08-07 11:00 | 8 | 7 | 11 | 75.41% | 22.14%
2024-08-07 12:00 | 8 | 7 | 12 | 75.41% | 22.67%
2024-08-07 13:00 | 8 | 7 | 13 | 75.41% | 23.04%
2024-08-07 14:00 | 8 | 7 | 14 | 71.1% | 22.81%
2024-08-07 15:00 | 8 | 7 | 15 | 58.36% | 22.15%
2024-08-07 16:00 | 8 | 7 | 16 | 41.13% | 21.59%
2024-08-07 17:00 | 8 | 7 | 17 | 21.38% | 20.96%
2024-08-07 18:00 | 8 | 7 | 18 | 6.047% | 20.54%
2024-08-07 19:00 | 8 | 7 | 19 | 2.639% | 21.32%
2024-08-07 20:00 | 8 | 7 | 20 | 0% | 22.61%
2024-08-07 21:00 | 8 | 7 | 21 | 0% | 23.63%
2024-08-07 22:00 | 8 | 7 | 22 | 0% | 23.7%
2024-08-07 23:00 | 8 | 7 | 23 | 0% | 23.71%
2024-08-08 | 8 | 8 | 0 | 0% | 30.61%
2024-08-08 01:00 | 8 | 8 | 1 | 0% | 22.86%
2024-08-08 02:00 | 8 | 8 | 2 | 0% | 21.53%
2024-08-08 03:00 | 8 | 8 | 3 | 0% | 20.86%
2024-08-08 04:00 | 8 | 8 | 4 | 0% | 20.36%
2024-08-08 05:00 | 8 | 8 | 5 | 3.547% | 18.87%
2024-08-08 06:00 | 8 | 8 | 6 | 10.28% | 17.38%
2024-08-08 07:00 | 8 | 8 | 7 | 22.34% | 16.98%
2024-08-08 08:00 | 8 | 8 | 8 | 35.53% | 17.58%
2024-08-08 09:00 | 8 | 8 | 9 | 41.83% | 19.26%
2024-08-08 10:00 | 8 | 8 | 10 | 27.95% | 19.61%
2024-08-08 11:00 | 8 | 8 | 11 | 60.06% | 21.64%
2024-08-08 12:00 | 8 | 8 | 12 | 75.41% | 23.52%
2024-08-08 13:00 | 8 | 8 | 13 | 75.41% | 24.9%
2024-08-08 14:00 | 8 | 8 | 14 | 70.44% | 26.1%
2024-08-08 15:00 | 8 | 8 | 15 | 57.7% | 27.36%
2024-08-08 16:00 | 8 | 8 | 16 | 37.62% | 27.67%
2024-08-08 17:00 | 8 | 8 | 17 | 19.47% | 27.45%
2024-08-08 18:00 | 8 | 8 | 18 | 6.547% | 27.13%
2024-08-08 19:00 | 8 | 8 | 19 | 2.031% | 27.87%
2024-08-08 20:00 | 8 | 8 | 20 | 0% | 29.38%
2024-08-08 21:00 | 8 | 8 | 21 | 0% | 31.07%
2024-08-08 22:00 | 8 | 8 | 22 | 0% | 31.31%
2024-08-08 23:00 | 8 | 8 | 23 | 0% | 31.11%
2024-08-09 | 8 | 9 | 0 | 0% | 31.78%
2024-08-09 01:00 | 8 | 9 | 1 | 0% | 29.61%
2024-08-09 02:00 | 8 | 9 | 2 | 0% | 30.26%
2024-08-09 03:00 | 8 | 9 | 3 | 0% | 28.09%
2024-08-09 04:00 | 8 | 9 | 4 | 0% | 29.39%
2024-08-09 05:00 | 8 | 9 | 5 | 2.41% | 26.08%
2024-08-09 06:00 | 8 | 9 | 6 | 8.664% | 24.8%
2024-08-09 07:00 | 8 | 9 | 7 | 26.24% | 24.06%
2024-08-09 08:00 | 8 | 9 | 8 | 48.57% | 24.07%
2024-08-09 09:00 | 8 | 9 | 9 | 63.71% | 24.73%
2024-08-09 10:00 | 8 | 9 | 10 | 69.89% | 25.62%
2024-08-09 11:00 | 8 | 9 | 11 | 73.42% | 26.91%
2024-08-09 12:00 | 8 | 9 | 12 | 58.13% | 26.97%
2024-08-09 13:00 | 8 | 9 | 13 | 70.05% | 27.04%
2024-08-09 14:00 | 8 | 9 | 14 | 66.17% | 27.25%
2024-08-09 15:00 | 8 | 9 | 15 | 56.73% | 26.88%
2024-08-09 16:00 | 8 | 9 | 16 | 31.69% | 26.63%
2024-08-09 17:00 | 8 | 9 | 17 | 20.3% | 28.11%
2024-08-09 18:00 | 8 | 9 | 18 | 5.856% | 25.78%
2024-08-09 19:00 | 8 | 9 | 19 | 2.316% | 26.72%
2024-08-09 20:00 | 8 | 9 | 20 | 0% | 28.05%
2024-08-09 21:00 | 8 | 9 | 21 | 0% | 29.2%
2024-08-09 22:00 | 8 | 9 | 22 | 0% | 29.66%
2024-08-09 23:00 | 8 | 9 | 23 | 0% | 31.02%
2024-08-10 | 8 | 10 | 0 | 0% | 30.98%
2024-08-10 01:00 | 8 | 10 | 1 | 0% | 32.09%
2024-08-10 02:00 | 8 | 10 | 2 | 0% | 32.29%
2024-08-10 03:00 | 8 | 10 | 3 | 0% | 31.97%
2024-08-10 04:00 | 8 | 10 | 4 | 0% | 31.88%
2024-08-10 05:00 | 8 | 10 | 5 | 0.3834% | 31.26%
2024-08-10 06:00 | 8 | 10 | 6 | 2.118% | 30.39%
2024-08-10 07:00 | 8 | 10 | 7 | 11.22% | 30.04%
2024-08-10 08:00 | 8 | 10 | 8 | 17.61% | 30.31%
2024-08-10 09:00 | 8 | 10 | 9 | 15.95% | 31.96%
2024-08-10 10:00 | 8 | 10 | 10 | 17.02% | 30.32%
2024-08-10 11:00 | 8 | 10 | 11 | 6.202% | 30.11%
2024-08-10 12:00 | 8 | 10 | 12 | 17.69% | 29.69%
2024-08-10 13:00 | 8 | 10 | 13 | 23.88% | 30.03%
2024-08-10 14:00 | 8 | 10 | 14 | 26.75% | 30.62%
2024-08-10 15:00 | 8 | 10 | 15 | 16.55% | 31.52%
2024-08-10 16:00 | 8 | 10 | 16 | 7.227% | 32.42%
2024-08-10 17:00 | 8 | 10 | 17 | 5.686% | 31.42%
2024-08-10 18:00 | 8 | 10 | 18 | 1.853% | 30.76%
2024-08-10 19:00 | 8 | 10 | 19 | 0.5034% | 30.74%
2024-08-10 20:00 | 8 | 10 | 20 | 0% | 31.77%
2024-08-10 21:00 | 8 | 10 | 21 | 0% | 32.31%
2024-08-10 22:00 | 8 | 10 | 22 | 0% | 32.73%
2024-08-10 23:00 | 8 | 10 | 23 | 0% | 31.46%
2024-08-11 | 8 | 11 | 0 | 0% | 28.17%
2024-08-11 01:00 | 8 | 11 | 1 | 0% | 30.23%
2024-08-11 02:00 | 8 | 11 | 2 | 0% | 29.03%
2024-08-11 03:00 | 8 | 11 | 3 | 0% | 28.14%
2024-08-11 04:00 | 8 | 11 | 4 | 0% | 26.86%
2024-08-11 05:00 | 8 | 11 | 5 | 0.903% | 25.42%
2024-08-11 06:00 | 8 | 11 | 6 | 7.781% | 23.13%
2024-08-11 07:00 | 8 | 11 | 7 | 15.9% | 20.91%
2024-08-11 08:00 | 8 | 11 | 8 | 23.19% | 19.74%
2024-08-11 09:00 | 8 | 11 | 9 | 12.2% | 18.91%
2024-08-11 10:00 | 8 | 11 | 10 | 32.24% | 20.71%
2024-08-11 11:00 | 8 | 11 | 11 | 64.84% | 19.54%
2024-08-11 12:00 | 8 | 11 | 12 | 59.55% | 22%
2024-08-11 13:00 | 8 | 11 | 13 | 67.31% | 21.47%
2024-08-11 14:00 | 8 | 11 | 14 | 66.25% | 22.77%
2024-08-11 15:00 | 8 | 11 | 15 | 53.58% | 24.2%
2024-08-11 16:00 | 8 | 11 | 16 | 22.36% | 24.35%
2024-08-11 17:00 | 8 | 11 | 17 | 2.599% | 23.75%
2024-08-11 18:00 | 8 | 11 | 18 | 1.853% | 24.76%
2024-08-11 19:00 | 8 | 11 | 19 | 0.5037% | 25.14%
2024-08-11 20:00 | 8 | 11 | 20 | 0% | 25.4%
2024-08-11 21:00 | 8 | 11 | 21 | 0% | 27.21%
2024-08-11 22:00 | 8 | 11 | 22 | 0% | 28.23%
2024-08-11 23:00 | 8 | 11 | 23 | 0% | 32.09%
2024-08-12 | 8 | 12 | 0 | 0% | 21.28%
2024-08-12 01:00 | 8 | 12 | 1 | 0% | 27.81%
2024-08-12 02:00 | 8 | 12 | 2 | 0% | 25.59%
2024-08-12 03:00 | 8 | 12 | 3 | 0% | 25.06%
2024-08-12 04:00 | 8 | 12 | 4 | 0% | 24.1%
2024-08-12 05:00 | 8 | 12 | 5 | 0.5569% | 22.66%
2024-08-12 06:00 | 8 | 12 | 6 | 3.451% | 20.84%
2024-08-12 07:00 | 8 | 12 | 7 | 7.389% | 18.79%
2024-08-12 08:00 | 8 | 12 | 8 | 14.97% | 17.89%
2024-08-12 09:00 | 8 | 12 | 9 | 15.54% | 17.99%
2024-08-12 10:00 | 8 | 12 | 10 | 16.01% | 16.5%
2024-08-12 11:00 | 8 | 12 | 11 | 18.26% | 18.54%
2024-08-12 12:00 | 8 | 12 | 12 | 22.91% | 18.86%
2024-08-12 13:00 | 8 | 12 | 13 | 18.51% | 19.23%
2024-08-12 14:00 | 8 | 12 | 14 | 19.44% | 19.16%
2024-08-12 15:00 | 8 | 12 | 15 | 21.06% | 18.98%
2024-08-12 16:00 | 8 | 12 | 16 | 17.44% | 18.18%
2024-08-12 17:00 | 8 | 12 | 17 | 11.91% | 17.54%
2024-08-12 18:00 | 8 | 12 | 18 | 5.154% | 17.38%
2024-08-12 19:00 | 8 | 12 | 19 | 0.5961% | 18.4%
2024-08-12 20:00 | 8 | 12 | 20 | 0% | 19.68%
2024-08-12 21:00 | 8 | 12 | 21 | 0% | 21.15%
2024-08-12 22:00 | 8 | 12 | 22 | 0% | 21.63%
2024-08-12 23:00 | 8 | 12 | 23 | 0% | 21.72%
2024-08-13 | 8 | 13 | 0 | 0% | 22.16%
2024-08-13 01:00 | 8 | 13 | 1 | 0% | 20.43%
2024-08-13 02:00 | 8 | 13 | 2 | 0% | 19.64%
2024-08-13 03:00 | 8 | 13 | 3 | 0% | 19.29%
2024-08-13 04:00 | 8 | 13 | 4 | 0% | 18.58%
2024-08-13 05:00 | 8 | 13 | 5 | 2.993% | 16.79%
2024-08-13 06:00 | 8 | 13 | 6 | 10.19% | 15.14%
2024-08-13 07:00 | 8 | 13 | 7 | 30.56% | 13.99%
2024-08-13 08:00 | 8 | 13 | 8 | 49.93% | 13.32%
2024-08-13 09:00 | 8 | 13 | 9 | 64.93% | 12.97%
2024-08-13 10:00 | 8 | 13 | 10 | 75.23% | 14.63%
2024-08-13 11:00 | 8 | 13 | 11 | 61.38% | 14.15%
2024-08-13 12:00 | 8 | 13 | 12 | 25.28% | 15.03%
2024-08-13 13:00 | 8 | 13 | 13 | 55.26% | 16.27%
2024-08-13 14:00 | 8 | 13 | 14 | 69.48% | 15.37%
2024-08-13 15:00 | 8 | 13 | 15 | 55.46% | 15.34%
2024-08-13 16:00 | 8 | 13 | 16 | 36.58% | 16.83%
2024-08-13 17:00 | 8 | 13 | 17 | 16.27% | 13.42%
2024-08-13 18:00 | 8 | 13 | 18 | 4.74% | 13.39%
2024-08-13 19:00 | 8 | 13 | 19 | 0.7646% | 14.51%
2024-08-13 20:00 | 8 | 13 | 20 | 0% | 16.83%
2024-08-13 21:00 | 8 | 13 | 21 | 0% | 19.18%
2024-08-13 22:00 | 8 | 13 | 22 | 0% | 20.59%
2024-08-13 23:00 | 8 | 13 | 23 | 0% | 21.42%
2024-08-14 | 8 | 14 | 0 | 0% | 25.42%
2024-08-14 01:00 | 8 | 14 | 1 | 0% | 21.77%
2024-08-14 02:00 | 8 | 14 | 2 | 0% | 21.78%
2024-08-14 03:00 | 8 | 14 | 3 | 0% | 21.54%
2024-08-14 04:00 | 8 | 14 | 4 | 0% | 20.93%
2024-08-14 05:00 | 8 | 14 | 5 | 2.629% | 19.89%
2024-08-14 06:00 | 8 | 14 | 6 | 10.48% | 18.64%
2024-08-14 07:00 | 8 | 14 | 7 | 24.24% | 17.76%
2024-08-14 08:00 | 8 | 14 | 8 | 35.46% | 16.31%
2024-08-14 09:00 | 8 | 14 | 9 | 56.48% | 16.46%
2024-08-14 10:00 | 8 | 14 | 10 | 74.37% | 17.3%
2024-08-14 11:00 | 8 | 14 | 11 | 71.11% | 18.04%
2024-08-14 12:00 | 8 | 14 | 12 | 65.18% | 19%
2024-08-14 13:00 | 8 | 14 | 13 | 59.92% | 19.7%
2024-08-14 14:00 | 8 | 14 | 14 | 56.93% | 19.94%
2024-08-14 15:00 | 8 | 14 | 15 | 38.45% | 19.59%
2024-08-14 16:00 | 8 | 14 | 16 | 39.25% | 19.09%
2024-08-14 17:00 | 8 | 14 | 17 | 18.17% | 18.72%
2024-08-14 18:00 | 8 | 14 | 18 | 5.433% | 18.61%
2024-08-14 19:00 | 8 | 14 | 19 | 0.9311% | 20.01%
2024-08-14 20:00 | 8 | 14 | 20 | 0% | 22.71%
2024-08-14 21:00 | 8 | 14 | 21 | 0% | 25.04%
2024-08-14 22:00 | 8 | 14 | 22 | 0% | 26.72%
2024-08-14 23:00 | 8 | 14 | 23 | 0% | 26.3%
2024-08-15 | 8 | 15 | 0 | 0% | 29.85%
2024-08-15 01:00 | 8 | 15 | 1 | 0% | 24.5%
2024-08-15 02:00 | 8 | 15 | 2 | 0% | 23.39%
2024-08-15 03:00 | 8 | 15 | 3 | 0% | 22.31%
2024-08-15 04:00 | 8 | 15 | 4 | 0% | 21.32%
2024-08-15 05:00 | 8 | 15 | 5 | 0.5599% | 19.67%
2024-08-15 06:00 | 8 | 15 | 6 | 0.716% | 17.34%
2024-08-15 07:00 | 8 | 15 | 7 | 1.111% | 15.09%
2024-08-15 08:00 | 8 | 15 | 8 | 6.017% | 14.63%
2024-08-15 09:00 | 8 | 15 | 9 | 8.015% | 15.95%
2024-08-15 10:00 | 8 | 15 | 10 | 11.6% | 17.76%
2024-08-15 11:00 | 8 | 15 | 11 | 4.527% | 19.52%
2024-08-15 12:00 | 8 | 15 | 12 | 8.279% | 22.15%
2024-08-15 13:00 | 8 | 15 | 13 | 10.32% | 24.24%
2024-08-15 14:00 | 8 | 15 | 14 | 13.42% | 25.59%
2024-08-15 15:00 | 8 | 15 | 15 | 11.31% | 26.98%
2024-08-15 16:00 | 8 | 15 | 16 | 14.3% | 28.2%
2024-08-15 17:00 | 8 | 15 | 17 | 16.38% | 25.68%
2024-08-15 18:00 | 8 | 15 | 18 | 4.512% | 25.46%
2024-08-15 19:00 | 8 | 15 | 19 | 1.017% | 26.53%
2024-08-15 20:00 | 8 | 15 | 20 | 0% | 28.25%
2024-08-15 21:00 | 8 | 15 | 21 | 0% | 29.98%
2024-08-15 22:00 | 8 | 15 | 22 | 0% | 30.54%
2024-08-15 23:00 | 8 | 15 | 23 | 0% | 30.18%
2024-08-16 | 8 | 16 | 0 | 0% | 26.82%
2024-08-16 01:00 | 8 | 16 | 1 | 0% | 29.11%
2024-08-16 02:00 | 8 | 16 | 2 | 0% | 28.22%
2024-08-16 03:00 | 8 | 16 | 3 | 0% | 27.17%
2024-08-16 04:00 | 8 | 16 | 4 | 0% | 26.78%
2024-08-16 05:00 | 8 | 16 | 5 | 0% | 25.58%
2024-08-16 06:00 | 8 | 16 | 6 | 1.239% | 24.13%
2024-08-16 07:00 | 8 | 16 | 7 | 2.885% | 22.53%
2024-08-16 08:00 | 8 | 16 | 8 | 6.804% | 22.17%
2024-08-16 09:00 | 8 | 16 | 9 | 14.87% | 22.75%
2024-08-16 10:00 | 8 | 16 | 10 | 47.75% | 23.23%
2024-08-16 11:00 | 8 | 16 | 11 | 45.84% | 23.67%
2024-08-16 12:00 | 8 | 16 | 12 | 21.71% | 23.78%
2024-08-16 13:00 | 8 | 16 | 13 | 18.01% | 23.78%
2024-08-16 14:00 | 8 | 16 | 14 | 21.89% | 23.67%
2024-08-16 15:00 | 8 | 16 | 15 | 7.672% | 24.15%
2024-08-16 16:00 | 8 | 16 | 16 | 6.459% | 23.38%
2024-08-16 17:00 | 8 | 16 | 17 | 7.8% | 22.26%
2024-08-16 18:00 | 8 | 16 | 18 | 1.79% | 21.55%
2024-08-16 19:00 | 8 | 16 | 19 | 0% | 21.89%
2024-08-16 20:00 | 8 | 16 | 20 | 0% | 23.55%
2024-08-16 21:00 | 8 | 16 | 21 | 0% | 25.1%
2024-08-16 22:00 | 8 | 16 | 22 | 0% | 26.1%
2024-08-16 23:00 | 8 | 16 | 23 | 0% | 26.6%
2024-08-17 | 8 | 17 | 0 | 0% | 23.47%
2024-08-17 01:00 | 8 | 17 | 1 | 0% | 26.95%
2024-08-17 02:00 | 8 | 17 | 2 | 0% | 26.96%
2024-08-17 03:00 | 8 | 17 | 3 | 0% | 26.57%
2024-08-17 04:00 | 8 | 17 | 4 | 0% | 26.52%
2024-08-17 05:00 | 8 | 17 | 5 | 1.65% | 26.04%
2024-08-17 06:00 | 8 | 17 | 6 | 7.734% | 24.47%
2024-08-17 07:00 | 8 | 17 | 7 | 25.75% | 23.45%
2024-08-17 08:00 | 8 | 17 | 8 | 42.94% | 24.01%
2024-08-17 09:00 | 8 | 17 | 9 | 62.06% | 24.93%
2024-08-17 10:00 | 8 | 17 | 10 | 65.16% | 25.22%
2024-08-17 11:00 | 8 | 17 | 11 | 52.5% | 25.76%
2024-08-17 12:00 | 8 | 17 | 12 | 68.33% | 26.11%
2024-08-17 13:00 | 8 | 17 | 13 | 34.49% | 26.59%
2024-08-17 14:00 | 8 | 17 | 14 | 36.73% | 26.92%
2024-08-17 15:00 | 8 | 17 | 15 | 35.52% | 26.38%
2024-08-17 16:00 | 8 | 17 | 16 | 21.57% | 25.01%
2024-08-17 17:00 | 8 | 17 | 17 | 15.86% | 23.61%
2024-08-17 18:00 | 8 | 17 | 18 | 4.977% | 22.47%
2024-08-17 19:00 | 8 | 17 | 19 | 0.8642% | 22.4%
2024-08-17 20:00 | 8 | 17 | 20 | 0% | 23.25%
2024-08-17 21:00 | 8 | 17 | 21 | 0% | 24.28%
2024-08-17 22:00 | 8 | 17 | 22 | 0% | 24.08%
2024-08-17 23:00 | 8 | 17 | 23 | 0% | 24.16%
2024-08-18 | 8 | 18 | 0 | 0% | 29.03%
2024-08-18 01:00 | 8 | 18 | 1 | 0% | 22.66%
2024-08-18 02:00 | 8 | 18 | 2 | 0% | 22.96%
2024-08-18 03:00 | 8 | 18 | 3 | 0% | 22.7%
2024-08-18 04:00 | 8 | 18 | 4 | 0% | 22.2%
2024-08-18 05:00 | 8 | 18 | 5 | 1.081% | 21.72%
2024-08-18 06:00 | 8 | 18 | 6 | 4.6% | 20.72%
2024-08-18 07:00 | 8 | 18 | 7 | 22.54% | 19.69%
2024-08-18 08:00 | 8 | 18 | 8 | 26.97% | 19.8%
2024-08-18 09:00 | 8 | 18 | 9 | 53.72% | 21.05%
2024-08-18 10:00 | 8 | 18 | 10 | 69.37% | 22.28%
2024-08-18 11:00 | 8 | 18 | 11 | 62.18% | 23.53%
2024-08-18 12:00 | 8 | 18 | 12 | 50.84% | 24.73%
2024-08-18 13:00 | 8 | 18 | 13 | 22.12% | 25.5%
2024-08-18 14:00 | 8 | 18 | 14 | 19.32% | 25.74%
2024-08-18 15:00 | 8 | 18 | 15 | 52.4% | 25.85%
2024-08-18 16:00 | 8 | 18 | 16 | 39.43% | 25.87%
2024-08-18 17:00 | 8 | 18 | 17 | 18.6% | 27.13%
2024-08-18 18:00 | 8 | 18 | 18 | 4.046% | 25.76%
2024-08-18 19:00 | 8 | 18 | 19 | 0.3487% | 26.59%
2024-08-18 20:00 | 8 | 18 | 20 | 0% | 28.36%
2024-08-18 21:00 | 8 | 18 | 21 | 0% | 29.89%
2024-08-18 22:00 | 8 | 18 | 22 | 0% | 30.01%
2024-08-18 23:00 | 8 | 18 | 23 | 0% | 29.53%
2024-08-19 | 8 | 19 | 0 | 0% | 24.54%
2024-08-19 01:00 | 8 | 19 | 1 | 0% | 28.23%
2024-08-19 02:00 | 8 | 19 | 2 | 0% | 27%
2024-08-19 03:00 | 8 | 19 | 3 | 0% | 24.39%
2024-08-19 04:00 | 8 | 19 | 4 | 0% | 25.39%
2024-08-19 05:00 | 8 | 19 | 5 | 0.8188% | 24.19%
2024-08-19 06:00 | 8 | 19 | 6 | 6.93% | 22.29%
2024-08-19 07:00 | 8 | 19 | 7 | 14.56% | 21.22%
2024-08-19 08:00 | 8 | 19 | 8 | 33.29% | 21.12%
2024-08-19 09:00 | 8 | 19 | 9 | 40.22% | 21.45%
2024-08-19 10:00 | 8 | 19 | 10 | 58.04% | 21.95%
2024-08-19 11:00 | 8 | 19 | 11 | 72.13% | 22.67%
2024-08-19 12:00 | 8 | 19 | 12 | 43.57% | 23.03%
2024-08-19 13:00 | 8 | 19 | 13 | 23.24% | 25.18%
2024-08-19 14:00 | 8 | 19 | 14 | 15.71% | 23.72%
2024-08-19 15:00 | 8 | 19 | 15 | 17.72% | 23.73%
2024-08-19 16:00 | 8 | 19 | 16 | 15.53% | 23.13%
2024-08-19 17:00 | 8 | 19 | 17 | 7.599% | 21.91%
2024-08-19 18:00 | 8 | 19 | 18 | 2.931% | 21.51%
2024-08-19 19:00 | 8 | 19 | 19 | 0% | 22.13%
2024-08-19 20:00 | 8 | 19 | 20 | 0% | 23.21%
2024-08-19 21:00 | 8 | 19 | 21 | 0% | 24.16%
2024-08-19 22:00 | 8 | 19 | 22 | 0% | 24.51%
2024-08-19 23:00 | 8 | 19 | 23 | 0% | 24.83%
2024-08-20 | 8 | 20 | 0 | 0% | 21.85%
2024-08-20 01:00 | 8 | 20 | 1 | 0% | 24.1%
2024-08-20 02:00 | 8 | 20 | 2 | 0% | 23.39%
2024-08-20 03:00 | 8 | 20 | 3 | 0% | 22.73%
2024-08-20 04:00 | 8 | 20 | 4 | 0% | 22.14%
2024-08-20 05:00 | 8 | 20 | 5 | 0.9729% | 21.33%
2024-08-20 06:00 | 8 | 20 | 6 | 6.428% | 19.29%
2024-08-20 07:00 | 8 | 20 | 7 | 13.26% | 15.73%
2024-08-20 08:00 | 8 | 20 | 8 | 41.31% | 15.86%
2024-08-20 09:00 | 8 | 20 | 9 | 47.17% | 15.87%
2024-08-20 10:00 | 8 | 20 | 10 | 54.64% | 16.15%
2024-08-20 11:00 | 8 | 20 | 11 | 56.82% | 16.69%
2024-08-20 12:00 | 8 | 20 | 12 | 38.44% | 17.11%
2024-08-20 13:00 | 8 | 20 | 13 | 17.74% | 17.25%
2024-08-20 14:00 | 8 | 20 | 14 | 11.2% | 17.15%
2024-08-20 15:00 | 8 | 20 | 15 | 16.14% | 17.31%
2024-08-20 16:00 | 8 | 20 | 16 | 12.32% | 17.04%
2024-08-20 17:00 | 8 | 20 | 17 | 7.916% | 16.01%
2024-08-20 18:00 | 8 | 20 | 18 | 3.061% | 16.19%
2024-08-20 19:00 | 8 | 20 | 19 | 0.167% | 18.15%
2024-08-20 20:00 | 8 | 20 | 20 | 0% | 19.94%
2024-08-20 21:00 | 8 | 20 | 21 | 0% | 21.26%
2024-08-20 22:00 | 8 | 20 | 22 | 0% | 22.68%
2024-08-20 23:00 | 8 | 20 | 23 | 0% | 21.9%
2024-08-21 | 8 | 21 | 0 | 0% | 23.48%
2024-08-21 01:00 | 8 | 21 | 1 | 0% | 21.55%
2024-08-21 02:00 | 8 | 21 | 2 | 0% | 20.98%
2024-08-21 03:00 | 8 | 21 | 3 | 0% | 20.34%
2024-08-21 04:00 | 8 | 21 | 4 | 0% | 19.48%
2024-08-21 05:00 | 8 | 21 | 5 | 0.7116% | 18.11%
2024-08-21 06:00 | 8 | 21 | 6 | 4.205% | 15.65%
2024-08-21 07:00 | 8 | 21 | 7 | 15.5% | 13.65%
2024-08-21 08:00 | 8 | 21 | 8 | 42.47% | 13.26%
2024-08-21 09:00 | 8 | 21 | 9 | 45.54% | 13.77%
2024-08-21 10:00 | 8 | 21 | 10 | 47.55% | 15.6%
2024-08-21 11:00 | 8 | 21 | 11 | 68.14% | 15.39%
2024-08-21 12:00 | 8 | 21 | 12 | 49.73% | 17.64%
2024-08-21 13:00 | 8 | 21 | 13 | 37.38% | 17.53%
2024-08-21 14:00 | 8 | 21 | 14 | 34.09% | 18.6%
2024-08-21 15:00 | 8 | 21 | 15 | 25.5% | 19.3%
2024-08-21 16:00 | 8 | 21 | 16 | 16.13% | 19.33%
2024-08-21 17:00 | 8 | 21 | 17 | 6.522% | 19.18%
2024-08-21 18:00 | 8 | 21 | 18 | 2.24% | 19.42%
2024-08-21 19:00 | 8 | 21 | 19 | 0% | 21.5%
2024-08-21 20:00 | 8 | 21 | 20 | 0% | 21.25%
2024-08-21 21:00 | 8 | 21 | 21 | 0% | 22.68%
2024-08-21 22:00 | 8 | 21 | 22 | 0% | 23.51%
2024-08-21 23:00 | 8 | 21 | 23 | 0% | 23.6%
2024-08-22 | 8 | 22 | 0 | 0% | 30.46%
2024-08-22 01:00 | 8 | 22 | 1 | 0% | 23.48%
2024-08-22 02:00 | 8 | 22 | 2 | 0% | 23.1%
2024-08-22 03:00 | 8 | 22 | 3 | 0% | 22.47%
2024-08-22 04:00 | 8 | 22 | 4 | 0% | 19.55%
2024-08-22 05:00 | 8 | 22 | 5 | 0% | 20.19%
2024-08-22 06:00 | 8 | 22 | 6 | 0.9736% | 18.54%
2024-08-22 07:00 | 8 | 22 | 7 | 6.46% | 17.36%
2024-08-22 08:00 | 8 | 22 | 8 | 12.77% | 17.69%
2024-08-22 09:00 | 8 | 22 | 9 | 8.368% | 18.71%
2024-08-22 10:00 | 8 | 22 | 10 | 14.57% | 20.31%
2024-08-22 11:00 | 8 | 22 | 11 | 16.82% | 22%
2024-08-22 12:00 | 8 | 22 | 12 | 21.41% | 24.13%
2024-08-22 13:00 | 8 | 22 | 13 | 33.02% | 25.28%
2024-08-22 14:00 | 8 | 22 | 14 | 54.09% | 25.91%
2024-08-22 15:00 | 8 | 22 | 15 | 44.06% | 26.32%
2024-08-22 16:00 | 8 | 22 | 16 | 26.05% | 26.63%
2024-08-22 17:00 | 8 | 22 | 17 | 14.09% | 29.26%
2024-08-22 18:00 | 8 | 22 | 18 | 3.026% | 26.75%
2024-08-22 19:00 | 8 | 22 | 19 | 0% | 27.46%
2024-08-22 20:00 | 8 | 22 | 20 | 0% | 29.06%
2024-08-22 21:00 | 8 | 22 | 21 | 0% | 30.31%
2024-08-22 22:00 | 8 | 22 | 22 | 0% | 30.82%
2024-08-22 23:00 | 8 | 22 | 23 | 0% | 30.75%
2024-08-23 | 8 | 23 | 0 | 0% | 28.95%
2024-08-23 01:00 | 8 | 23 | 1 | 0% | 29.66%
2024-08-23 02:00 | 8 | 23 | 2 | 0% | 28.85%
2024-08-23 03:00 | 8 | 23 | 3 | 0% | 27.85%
2024-08-23 04:00 | 8 | 23 | 4 | 0% | 26.94%
2024-08-23 05:00 | 8 | 23 | 5 | 0% | 25.76%
2024-08-23 06:00 | 8 | 23 | 6 | 2.732% | 23.93%
2024-08-23 07:00 | 8 | 23 | 7 | 10.07% | 21.94%
2024-08-23 08:00 | 8 | 23 | 8 | 8.287% | 20.89%
2024-08-23 09:00 | 8 | 23 | 9 | 9.159% | 20.82%
2024-08-23 10:00 | 8 | 23 | 10 | 10.04% | 22.7%
2024-08-23 11:00 | 8 | 23 | 11 | 12.78% | 21.41%
2024-08-23 12:00 | 8 | 23 | 12 | 14.53% | 22.37%
2024-08-23 13:00 | 8 | 23 | 13 | 13.13% | 25.56%
2024-08-23 14:00 | 8 | 23 | 14 | 10.29% | 24.77%
2024-08-23 15:00 | 8 | 23 | 15 | 8.058% | 26.13%
2024-08-23 16:00 | 8 | 23 | 16 | 6.054% | 26.42%
2024-08-23 17:00 | 8 | 23 | 17 | 3.144% | 28.68%
2024-08-23 18:00 | 8 | 23 | 18 | 1.241% | 26.91%
2024-08-23 19:00 | 8 | 23 | 19 | 0% | 28.04%
2024-08-23 20:00 | 8 | 23 | 20 | 0% | 29.26%
2024-08-23 21:00 | 8 | 23 | 21 | 0% | 30.48%
2024-08-23 22:00 | 8 | 23 | 22 | 0% | 30.22%
2024-08-23 23:00 | 8 | 23 | 23 | 0% | 29.86%
2024-08-24 | 8 | 24 | 0 | 0% | 31.78%
2024-08-24 01:00 | 8 | 24 | 1 | 0% | 27.7%
2024-08-24 02:00 | 8 | 24 | 2 | 0% | 26.48%
2024-08-24 03:00 | 8 | 24 | 3 | 0% | 25.44%
2024-08-24 04:00 | 8 | 24 | 4 | 0% | 24.48%
2024-08-24 05:00 | 8 | 24 | 5 | 0.788% | 22.8%
2024-08-24 06:00 | 8 | 24 | 6 | 4.835% | 21.21%
2024-08-24 07:00 | 8 | 24 | 7 | 9.035% | 19.18%
2024-08-24 08:00 | 8 | 24 | 8 | 12.03% | 17.59%
2024-08-24 09:00 | 8 | 24 | 9 | 42.97% | 16.48%
2024-08-24 10:00 | 8 | 24 | 10 | 66.73% | 16.01%
2024-08-24 11:00 | 8 | 24 | 11 | 75.41% | 17.07%
2024-08-24 12:00 | 8 | 24 | 12 | 75.41% | 16.47%
2024-08-24 13:00 | 8 | 24 | 13 | 72.87% | 18.89%
2024-08-24 14:00 | 8 | 24 | 14 | 49.55% | 17.97%
2024-08-24 15:00 | 8 | 24 | 15 | 40.19% | 19.24%
2024-08-24 16:00 | 8 | 24 | 16 | 34.29% | 19.49%
2024-08-24 17:00 | 8 | 24 | 17 | 15.1% | 19.76%
2024-08-24 18:00 | 8 | 24 | 18 | 2.994% | 20.86%
2024-08-24 19:00 | 8 | 24 | 19 | 0% | 23.41%
2024-08-24 20:00 | 8 | 24 | 20 | 0% | 25.99%
2024-08-24 21:00 | 8 | 24 | 21 | 0% | 28.64%
2024-08-24 22:00 | 8 | 24 | 22 | 0% | 29.96%
2024-08-24 23:00 | 8 | 24 | 23 | 0% | 31.24%
2024-08-25 | 8 | 25 | 0 | 0% | 26.26%
2024-08-25 01:00 | 8 | 25 | 1 | 0% | 30.95%
2024-08-25 02:00 | 8 | 25 | 2 | 0% | 29.74%
2024-08-25 03:00 | 8 | 25 | 3 | 0% | 28.5%
2024-08-25 04:00 | 8 | 25 | 4 | 0% | 27.26%
2024-08-25 05:00 | 8 | 25 | 5 | 0% | 25.72%
2024-08-25 06:00 | 8 | 25 | 6 | 1.156% | 25.07%
2024-08-25 07:00 | 8 | 25 | 7 | 5.015% | 21.75%
2024-08-25 08:00 | 8 | 25 | 8 | 9.719% | 21.39%
2024-08-25 09:00 | 8 | 25 | 9 | 15.94% | 22.02%
2024-08-25 10:00 | 8 | 25 | 10 | 16.76% | 22.26%
2024-08-25 11:00 | 8 | 25 | 11 | 30.33% | 23.27%
2024-08-25 12:00 | 8 | 25 | 12 | 31.67% | 24.33%
2024-08-25 13:00 | 8 | 25 | 13 | 46.87% | 27.28%
2024-08-25 14:00 | 8 | 25 | 14 | 61.39% | 25.2%
2024-08-25 15:00 | 8 | 25 | 15 | 42.48% | 25.38%
2024-08-25 16:00 | 8 | 25 | 16 | 35.93% | 26.06%
2024-08-25 17:00 | 8 | 25 | 17 | 15.02% | 27.17%
2024-08-25 18:00 | 8 | 25 | 18 | 3.21% | 20.73%
2024-08-25 19:00 | 8 | 25 | 19 | 0% | 27.16%
2024-08-25 20:00 | 8 | 25 | 20 | 0% | 26.67%
2024-08-25 21:00 | 8 | 25 | 21 | 0% | 28.64%
2024-08-25 22:00 | 8 | 25 | 22 | 0% | 24.84%
2024-08-25 23:00 | 8 | 25 | 23 | 0% | 26.35%
2024-08-26 | 8 | 26 | 0 | 0% | 30.23%
2024-08-26 01:00 | 8 | 26 | 1 | 0% | 25.68%
2024-08-26 02:00 | 8 | 26 | 2 | 0% | 26.8%
2024-08-26 03:00 | 8 | 26 | 3 | 0% | 25.61%
2024-08-26 04:00 | 8 | 26 | 4 | 0% | 25.99%
2024-08-26 05:00 | 8 | 26 | 5 | 0.4604% | 26.28%
2024-08-26 06:00 | 8 | 26 | 6 | 2.678% | 25.74%
2024-08-26 07:00 | 8 | 26 | 7 | 17.65% | 24.45%
2024-08-26 08:00 | 8 | 26 | 8 | 24.55% | 25.99%
2024-08-26 09:00 | 8 | 26 | 9 | 57.78% | 26.36%
2024-08-26 10:00 | 8 | 26 | 10 | 70.06% | 25.11%
2024-08-26 11:00 | 8 | 26 | 11 | 71.26% | 25.88%
2024-08-26 12:00 | 8 | 26 | 12 | 75.41% | 26.55%
2024-08-26 13:00 | 8 | 26 | 13 | 63.09% | 27.25%
2024-08-26 14:00 | 8 | 26 | 14 | 30.43% | 27.85%
2024-08-26 15:00 | 8 | 26 | 15 | 20.47% | 28.65%
2024-08-26 16:00 | 8 | 26 | 16 | 13.25% | 29.06%
2024-08-26 17:00 | 8 | 26 | 17 | 7.892% | 28.94%
2024-08-26 18:00 | 8 | 26 | 18 | 3.088% | 29.26%
2024-08-26 19:00 | 8 | 26 | 19 | 0% | 30.24%
2024-08-26 20:00 | 8 | 26 | 20 | 0% | 30.86%
2024-08-26 21:00 | 8 | 26 | 21 | 0% | 29.06%
2024-08-26 22:00 | 8 | 26 | 22 | 0% | 31.43%
2024-08-26 23:00 | 8 | 26 | 23 | 0% | 30.63%
2024-08-27 | 8 | 27 | 0 | 0% | 22.16%
2024-08-27 01:00 | 8 | 27 | 1 | 0% | 29.62%
2024-08-27 02:00 | 8 | 27 | 2 | 0% | 29.45%
2024-08-27 03:00 | 8 | 27 | 3 | 0% | 28.56%
2024-08-27 04:00 | 8 | 27 | 4 | 0% | 28.21%
2024-08-27 05:00 | 8 | 27 | 5 | 0.6293% | 27%
2024-08-27 06:00 | 8 | 27 | 6 | 6.97% | 25.56%
2024-08-27 07:00 | 8 | 27 | 7 | 15.55% | 24.24%
2024-08-27 08:00 | 8 | 27 | 8 | 25.17% | 23.88%
2024-08-27 09:00 | 8 | 27 | 9 | 37.89% | 23.72%
2024-08-27 10:00 | 8 | 27 | 10 | 63.36% | 23.55%
2024-08-27 11:00 | 8 | 27 | 11 | 42% | 23.5%
2024-08-27 12:00 | 8 | 27 | 12 | 18.6% | 23.69%
2024-08-27 13:00 | 8 | 27 | 13 | 5.012% | 23.57%
2024-08-27 14:00 | 8 | 27 | 14 | 9.155% | 23.33%
2024-08-27 15:00 | 8 | 27 | 15 | 15.35% | 22.5%
2024-08-27 16:00 | 8 | 27 | 16 | 23.5% | 21.52%
2024-08-27 17:00 | 8 | 27 | 17 | 5.117% | 20.17%
2024-08-27 18:00 | 8 | 27 | 18 | 2.932% | 19.7%
2024-08-27 19:00 | 8 | 27 | 19 | 0% | 20.59%
2024-08-27 20:00 | 8 | 27 | 20 | 0% | 21.44%
2024-08-27 21:00 | 8 | 27 | 21 | 0% | 22.4%
2024-08-27 22:00 | 8 | 27 | 22 | 0% | 20.11%
2024-08-27 23:00 | 8 | 27 | 23 | 0% | 22.39%
2024-08-28 | 8 | 28 | 0 | 0% | 29.85%
2024-08-28 01:00 | 8 | 28 | 1 | 0% | 21.75%
2024-08-28 02:00 | 8 | 28 | 2 | 0% | 21.09%
2024-08-28 03:00 | 8 | 28 | 3 | 0% | 20.83%
2024-08-28 04:00 | 8 | 28 | 4 | 0% | 20.88%
2024-08-28 05:00 | 8 | 28 | 5 | 1.114% | 21.09%
2024-08-28 06:00 | 8 | 28 | 6 | 9.181% | 19.93%
2024-08-28 07:00 | 8 | 28 | 7 | 29.65% | 18.84%
2024-08-28 08:00 | 8 | 28 | 8 | 51.13% | 18.48%
2024-08-28 09:00 | 8 | 28 | 9 | 67.26% | 18.76%
2024-08-28 10:00 | 8 | 28 | 10 | 75.41% | 19.21%
2024-08-28 11:00 | 8 | 28 | 11 | 75.41% | 19.37%
2024-08-28 12:00 | 8 | 28 | 12 | 75.41% | 20%
2024-08-28 13:00 | 8 | 28 | 13 | 75.41% | 20.65%
2024-08-28 14:00 | 8 | 28 | 14 | 71.35% | 21.42%
2024-08-28 15:00 | 8 | 28 | 15 | 57.08% | 21.72%
2024-08-28 16:00 | 8 | 28 | 16 | 31.37% | 21.75%
2024-08-28 17:00 | 8 | 28 | 17 | 11.19% | 21.51%
2024-08-28 18:00 | 8 | 28 | 18 | 2.336% | 22.13%
2024-08-28 19:00 | 8 | 28 | 19 | 0% | 23.92%
2024-08-28 20:00 | 8 | 28 | 20 | 0% | 26.07%
2024-08-28 21:00 | 8 | 28 | 21 | 0% | 28.28%
2024-08-28 22:00 | 8 | 28 | 22 | 0% | 29.46%
2024-08-28 23:00 | 8 | 28 | 23 | 0% | 34.34%
2024-08-29 | 8 | 29 | 0 | 0% | 21.67%
2024-08-29 01:00 | 8 | 29 | 1 | 0% | 29.66%
2024-08-29 02:00 | 8 | 29 | 2 | 0% | 29.64%
2024-08-29 03:00 | 8 | 29 | 3 | 0% | 29.37%
2024-08-29 04:00 | 8 | 29 | 4 | 0% | 29.45%
2024-08-29 05:00 | 8 | 29 | 5 | 1.1% | 28.79%
2024-08-29 06:00 | 8 | 29 | 6 | 7.933% | 27.01%
2024-08-29 07:00 | 8 | 29 | 7 | 28.69% | 25.04%
2024-08-29 08:00 | 8 | 29 | 8 | 42.65% | 23.96%
2024-08-29 09:00 | 8 | 29 | 9 | 54.37% | 23.17%
2024-08-29 10:00 | 8 | 29 | 10 | 69.72% | 23.46%
2024-08-29 11:00 | 8 | 29 | 11 | 75.41% | 23.76%
2024-08-29 12:00 | 8 | 29 | 12 | 75.41% | 24.43%
2024-08-29 13:00 | 8 | 29 | 13 | 72.54% | 24.8%
2024-08-29 14:00 | 8 | 29 | 14 | 70.13% | 25.1%
2024-08-29 15:00 | 8 | 29 | 15 | 52.8% | 24.49%
2024-08-29 16:00 | 8 | 29 | 16 | 22.42% | 23.39%
2024-08-29 17:00 | 8 | 29 | 17 | 10.53% | 22.14%
2024-08-29 18:00 | 8 | 29 | 18 | 2.66% | 21.61%
2024-08-29 19:00 | 8 | 29 | 19 | 0% | 22.12%
2024-08-29 20:00 | 8 | 29 | 20 | 0% | 22.82%
2024-08-29 21:00 | 8 | 29 | 21 | 0% | 23.14%
2024-08-29 22:00 | 8 | 29 | 22 | 0% | 23%
2024-08-29 23:00 | 8 | 29 | 23 | 0% | 22.36%
2024-08-30 | 8 | 30 | 0 | 0% | 20.87%
2024-08-30 01:00 | 8 | 30 | 1 | 0% | 21.23%
2024-08-30 02:00 | 8 | 30 | 2 | 0% | 20.52%
2024-08-30 03:00 | 8 | 30 | 3 | 0% | 20.07%
2024-08-30 04:00 | 8 | 30 | 4 | 0% | 19.3%
2024-08-30 05:00 | 8 | 30 | 5 | 0.383% | 18.88%
2024-08-30 06:00 | 8 | 30 | 6 | 1.452% | 17.03%
2024-08-30 07:00 | 8 | 30 | 7 | 7.324% | 14.6%
2024-08-30 08:00 | 8 | 30 | 8 | 17.72% | 13.49%
2024-08-30 09:00 | 8 | 30 | 9 | 46.24% | 13.51%
2024-08-30 10:00 | 8 | 30 | 10 | 25.9% | 14.19%
2024-08-30 11:00 | 8 | 30 | 11 | 56.56% | 15.18%
2024-08-30 12:00 | 8 | 30 | 12 | 71.32% | 16.12%
2024-08-30 13:00 | 8 | 30 | 13 | 72.06% | 16.63%
2024-08-30 14:00 | 8 | 30 | 14 | 69.34% | 16.78%
2024-08-30 15:00 | 8 | 30 | 15 | 47.38% | 17.14%
2024-08-30 16:00 | 8 | 30 | 16 | 5.661% | 17.73%
2024-08-30 17:00 | 8 | 30 | 17 | 12.43% | 15.87%
2024-08-30 18:00 | 8 | 30 | 18 | 2.297% | 15.59%
2024-08-30 19:00 | 8 | 30 | 19 | 0% | 16.87%
2024-08-30 20:00 | 8 | 30 | 20 | 0% | 18.15%
2024-08-30 21:00 | 8 | 30 | 21 | 0% | 20.73%
2024-08-30 22:00 | 8 | 30 | 22 | 0% | 20.51%
2024-08-30 23:00 | 8 | 30 | 23 | 0% | 20.96%
2024-08-31 | 8 | 31 | 0 | 0% | 25.17%
2024-08-31 01:00 | 8 | 31 | 1 | 0% | 20.91%
2024-08-31 02:00 | 8 | 31 | 2 | 0% | 20.68%
2024-08-31 03:00 | 8 | 31 | 3 | 0% | 20.67%
2024-08-31 04:00 | 8 | 31 | 4 | 0% | 20.77%
2024-08-31 05:00 | 8 | 31 | 5 | 0% | 20.25%
2024-08-31 06:00 | 8 | 31 | 6 | 0.8294% | 18.91%
2024-08-31 07:00 | 8 | 31 | 7 | 2.131% | 17.49%
2024-08-31 08:00 | 8 | 31 | 8 | 5.799% | 15.82%
2024-08-31 09:00 | 8 | 31 | 9 | 8.114% | 15.48%
2024-08-31 10:00 | 8 | 31 | 10 | 7.002% | 16%
2024-08-31 11:00 | 8 | 31 | 11 | 10.65% | 15.58%
2024-08-31 12:00 | 8 | 31 | 12 | 23.15% | 16.13%
2024-08-31 13:00 | 8 | 31 | 13 | 23.26% | 16.4%
2024-08-31 14:00 | 8 | 31 | 14 | 12.75% | 16.06%
2024-08-31 15:00 | 8 | 31 | 15 | 17.23% | 15.97%
2024-08-31 16:00 | 8 | 31 | 16 | 24.11% | 15.24%
2024-08-31 17:00 | 8 | 31 | 17 | 5.733% | 14.81%
2024-08-31 18:00 | 8 | 31 | 18 | 2.314% | 15.12%
2024-08-31 19:00 | 8 | 31 | 19 | 0% | 16.41%
2024-08-31 20:00 | 8 | 31 | 20 | 0% | 18.75%
2024-08-31 21:00 | 8 | 31 | 21 | 0% | 20.59%
2024-08-31 22:00 | 8 | 31 | 22 | 0% | 22.76%
2024-08-31 23:00 | 8 | 31 | 23 | 0% | 24.59%
2024-09-01 | 9 | 1 | 0 | 0% | 25.39%
2024-09-01 01:00 | 9 | 1 | 1 | 0% | 25.61%
2024-09-01 02:00 | 9 | 1 | 2 | 0% | 25.55%
2024-09-01 03:00 | 9 | 1 | 3 | 0% | 25.75%
2024-09-01 04:00 | 9 | 1 | 4 | 0% | 25.71%
2024-09-01 05:00 | 9 | 1 | 5 | 0% | 24.61%
2024-09-01 06:00 | 9 | 1 | 6 | 2.391% | 22.57%
2024-09-01 07:00 | 9 | 1 | 7 | 8.387% | 19.22%
2024-09-01 08:00 | 9 | 1 | 8 | 19.73% | 17.2%
2024-09-01 09:00 | 9 | 1 | 9 | 23.76% | 16.4%
2024-09-01 10:00 | 9 | 1 | 10 | 47.07% | 16.94%
2024-09-01 11:00 | 9 | 1 | 11 | 55.21% | 17.73%
2024-09-01 12:00 | 9 | 1 | 12 | 63.25% | 20.04%
2024-09-01 13:00 | 9 | 1 | 13 | 45.65% | 19.5%
2024-09-01 14:00 | 9 | 1 | 14 | 49.43% | 20.14%
2024-09-01 15:00 | 9 | 1 | 15 | 43.69% | 20.76%
2024-09-01 16:00 | 9 | 1 | 16 | 27.72% | 20.45%
2024-09-01 17:00 | 9 | 1 | 17 | 8.23% | 20.45%
2024-09-01 18:00 | 9 | 1 | 18 | 1.586% | 21.06%
2024-09-01 19:00 | 9 | 1 | 19 | 0% | 23.17%
2024-09-01 20:00 | 9 | 1 | 20 | 0% | 24.79%
2024-09-01 21:00 | 9 | 1 | 21 | 0% | 26.18%
2024-09-01 22:00 | 9 | 1 | 22 | 0% | 26.57%
2024-09-01 23:00 | 9 | 1 | 23 | 0% | 26.38%
2024-09-02 | 9 | 2 | 0 | 0% | 19.67%
2024-09-02 01:00 | 9 | 2 | 1 | 0% | 24.28%
2024-09-02 02:00 | 9 | 2 | 2 | 0% | 23.16%
2024-09-02 03:00 | 9 | 2 | 3 | 0% | 23.72%
2024-09-02 04:00 | 9 | 2 | 4 | 0% | 21.22%
2024-09-02 05:00 | 9 | 2 | 5 | 0.2002% | 20.31%
2024-09-02 06:00 | 9 | 2 | 6 | 4.85% | 18.81%
2024-09-02 07:00 | 9 | 2 | 7 | 20.68% | 16.66%
2024-09-02 08:00 | 9 | 2 | 8 | 28.27% | 15.27%
2024-09-02 09:00 | 9 | 2 | 9 | 26.7% | 14.88%
2024-09-02 10:00 | 9 | 2 | 10 | 24.61% | 16.31%
2024-09-02 11:00 | 9 | 2 | 11 | 22.16% | 15.69%
2024-09-02 12:00 | 9 | 2 | 12 | 12.46% | 16.57%
2024-09-02 13:00 | 9 | 2 | 13 | 5.57% | 17.07%
2024-09-02 14:00 | 9 | 2 | 14 | 5.662% | 17.55%
2024-09-02 15:00 | 9 | 2 | 15 | 4.72% | 17.51%
2024-09-02 16:00 | 9 | 2 | 16 | 4.843% | 16.84%
2024-09-02 17:00 | 9 | 2 | 17 | 2.738% | 16.64%
2024-09-02 18:00 | 9 | 2 | 18 | 0.4635% | 17.61%
2024-09-02 19:00 | 9 | 2 | 19 | 0% | 18.72%
2024-09-02 20:00 | 9 | 2 | 20 | 0% | 20.49%
2024-09-02 21:00 | 9 | 2 | 21 | 0% | 20.77%
2024-09-02 22:00 | 9 | 2 | 22 | 0% | 20.78%
2024-09-02 23:00 | 9 | 2 | 23 | 0% | 20.66%
2024-09-03 | 9 | 3 | 0 | 0% | 31.16%
2024-09-03 01:00 | 9 | 3 | 1 | 0% | 18.73%
2024-09-03 02:00 | 9 | 3 | 2 | 0% | 18.32%
2024-09-03 03:00 | 9 | 3 | 3 | 0% | 17.86%
2024-09-03 04:00 | 9 | 3 | 4 | 0% | 18.18%
2024-09-03 05:00 | 9 | 3 | 5 | 0% | 18.21%
2024-09-03 06:00 | 9 | 3 | 6 | 2.213% | 17.76%
2024-09-03 07:00 | 9 | 3 | 7 | 12.65% | 16.31%
2024-09-03 08:00 | 9 | 3 | 8 | 15.74% | 16%
2024-09-03 09:00 | 9 | 3 | 9 | 43.11% | 16.2%
2024-09-03 10:00 | 9 | 3 | 10 | 48.1% | 16.51%
2024-09-03 11:00 | 9 | 3 | 11 | 26.55% | 18.13%
2024-09-03 12:00 | 9 | 3 | 12 | 23.45% | 17.29%
2024-09-03 13:00 | 9 | 3 | 13 | 29.74% | 18%
2024-09-03 14:00 | 9 | 3 | 14 | 48.63% | 18.53%
2024-09-03 15:00 | 9 | 3 | 15 | 42.1% | 19.01%
2024-09-03 16:00 | 9 | 3 | 16 | 23.81% | 18.96%
2024-09-03 17:00 | 9 | 3 | 17 | 8.711% | 19.16%
2024-09-03 18:00 | 9 | 3 | 18 | 1.114% | 20.92%
2024-09-03 19:00 | 9 | 3 | 19 | 0% | 24.25%
2024-09-03 20:00 | 9 | 3 | 20 | 0% | 26.67%
2024-09-03 21:00 | 9 | 3 | 21 | 0% | 29.31%
2024-09-03 22:00 | 9 | 3 | 22 | 0% | 30.68%
2024-09-03 23:00 | 9 | 3 | 23 | 0% | 31.07%
2024-09-04 | 9 | 4 | 0 | 0% | 29.34%
2024-09-04 01:00 | 9 | 4 | 1 | 0% | 30.68%
2024-09-04 02:00 | 9 | 4 | 2 | 0% | 30.29%
2024-09-04 03:00 | 9 | 4 | 3 | 0% | 29.85%
2024-09-04 04:00 | 9 | 4 | 4 | 0% | 29.14%
2024-09-04 05:00 | 9 | 4 | 5 | 0.242% | 28.23%
2024-09-04 06:00 | 9 | 4 | 6 | 5.33% | 26.15%
2024-09-04 07:00 | 9 | 4 | 7 | 19.76% | 22.72%
2024-09-04 08:00 | 9 | 4 | 8 | 38.6% | 20.77%
2024-09-04 09:00 | 9 | 4 | 9 | 35.44% | 19.41%
2024-09-04 10:00 | 9 | 4 | 10 | 58.72% | 19.27%
2024-09-04 11:00 | 9 | 4 | 11 | 63.5% | 21.7%
2024-09-04 12:00 | 9 | 4 | 12 | 56.77% | 20.47%
2024-09-04 13:00 | 9 | 4 | 13 | 42.09% | 21.5%
2024-09-04 14:00 | 9 | 4 | 14 | 51.4% | 22.34%
2024-09-04 15:00 | 9 | 4 | 15 | 50.76% | 22.72%
2024-09-04 16:00 | 9 | 4 | 16 | 31.11% | 23.41%
2024-09-04 17:00 | 9 | 4 | 17 | 10.64% | 24.04%
2024-09-04 18:00 | 9 | 4 | 18 | 1.032% | 26.19%
2024-09-04 19:00 | 9 | 4 | 19 | 0% | 28.53%
2024-09-04 20:00 | 9 | 4 | 20 | 0% | 29.95%
2024-09-04 21:00 | 9 | 4 | 21 | 0% | 30.7%
2024-09-04 22:00 | 9 | 4 | 22 | 0% | 30.61%
2024-09-04 23:00 | 9 | 4 | 23 | 0% | 30.27%
2024-09-05 | 9 | 5 | 0 | 0% | 23.6%
2024-09-05 01:00 | 9 | 5 | 1 | 0% | 28.14%
2024-09-05 02:00 | 9 | 5 | 2 | 0% | 27.44%
2024-09-05 03:00 | 9 | 5 | 3 | 0% | 26.86%
2024-09-05 04:00 | 9 | 5 | 4 | 0% | 28.96%
2024-09-05 05:00 | 9 | 5 | 5 | 0% | 26.32%
2024-09-05 06:00 | 9 | 5 | 6 | 6.816% | 24.96%
2024-09-05 07:00 | 9 | 5 | 7 | 26.5% | 22.22%
2024-09-05 08:00 | 9 | 5 | 8 | 46.77% | 20.34%
2024-09-05 09:00 | 9 | 5 | 9 | 63.08% | 16.81%
2024-09-05 10:00 | 9 | 5 | 10 | 74.11% | 19.72%
2024-09-05 11:00 | 9 | 5 | 11 | 75.41% | 20.26%
2024-09-05 12:00 | 9 | 5 | 12 | 75.41% | 20.29%
2024-09-05 13:00 | 9 | 5 | 13 | 75.27% | 20.18%
2024-09-05 14:00 | 9 | 5 | 14 | 55.88% | 19.89%
2024-09-05 15:00 | 9 | 5 | 15 | 51.3% | 19.71%
2024-09-05 16:00 | 9 | 5 | 16 | 31.16% | 19.63%
2024-09-05 17:00 | 9 | 5 | 17 | 10.36% | 21.27%
2024-09-05 18:00 | 9 | 5 | 18 | 0.8554% | 20.34%
2024-09-05 19:00 | 9 | 5 | 19 | 0% | 21.67%
2024-09-05 20:00 | 9 | 5 | 20 | 0% | 22.92%
2024-09-05 21:00 | 9 | 5 | 21 | 0% | 23.8%
2024-09-05 22:00 | 9 | 5 | 22 | 0% | 24.01%
2024-09-05 23:00 | 9 | 5 | 23 | 0% | 24.08%
2024-09-06 | 9 | 6 | 0 | 0% | 25.47%
2024-09-06 01:00 | 9 | 6 | 1 | 0% | 23.09%
2024-09-06 02:00 | 9 | 6 | 2 | 0% | 23.04%
2024-09-06 03:00 | 9 | 6 | 3 | 0% | 23.08%
2024-09-06 04:00 | 9 | 6 | 4 | 0% | 23.26%
2024-09-06 05:00 | 9 | 6 | 5 | 0% | 22.8%
2024-09-06 06:00 | 9 | 6 | 6 | 4.534% | 21.78%
2024-09-06 07:00 | 9 | 6 | 7 | 25.38% | 19.55%
2024-09-06 08:00 | 9 | 6 | 8 | 35.35% | 17.99%
2024-09-06 09:00 | 9 | 6 | 9 | 60.99% | 17.47%
2024-09-06 10:00 | 9 | 6 | 10 | 71.97% | 17.86%
2024-09-06 11:00 | 9 | 6 | 11 | 75.41% | 18.48%
2024-09-06 12:00 | 9 | 6 | 12 | 75.41% | 19.14%
2024-09-06 13:00 | 9 | 6 | 13 | 73.24% | 19.61%
2024-09-06 14:00 | 9 | 6 | 14 | 63.92% | 19.57%
2024-09-06 15:00 | 9 | 6 | 15 | 49.03% | 19.61%
2024-09-06 16:00 | 9 | 6 | 16 | 29.1% | 19.17%
2024-09-06 17:00 | 9 | 6 | 17 | 7.934% | 19.03%
2024-09-06 18:00 | 9 | 6 | 18 | 0.8169% | 20.32%
2024-09-06 19:00 | 9 | 6 | 19 | 0% | 22.59%
2024-09-06 20:00 | 9 | 6 | 20 | 0% | 24.61%
2024-09-06 21:00 | 9 | 6 | 21 | 0% | 25.95%
2024-09-06 22:00 | 9 | 6 | 22 | 0% | 26.34%
2024-09-06 23:00 | 9 | 6 | 23 | 0% | 26.04%
2024-09-07 | 9 | 7 | 0 | 0% | 27.74%
2024-09-07 01:00 | 9 | 7 | 1 | 0% | 24.54%
2024-09-07 02:00 | 9 | 7 | 2 | 0% | 23.79%
2024-09-07 03:00 | 9 | 7 | 3 | 0% | 23.19%
2024-09-07 04:00 | 9 | 7 | 4 | 0% | 22.94%
2024-09-07 05:00 | 9 | 7 | 5 | 0% | 22.51%
2024-09-07 06:00 | 9 | 7 | 6 | 1.308% | 20.89%
2024-09-07 07:00 | 9 | 7 | 7 | 4.387% | 18.26%
2024-09-07 08:00 | 9 | 7 | 8 | 9.288% | 16.66%
2024-09-07 09:00 | 9 | 7 | 9 | 14.19% | 15.76%
2024-09-07 10:00 | 9 | 7 | 10 | 13.27% | 15.44%
2024-09-07 11:00 | 9 | 7 | 11 | 14.76% | 16.05%
2024-09-07 12:00 | 9 | 7 | 12 | 14.65% | 17.13%
2024-09-07 13:00 | 9 | 7 | 13 | 17.67% | 18.31%
2024-09-07 14:00 | 9 | 7 | 14 | 14.9% | 19.3%
2024-09-07 15:00 | 9 | 7 | 15 | 8.936% | 20.08%
2024-09-07 16:00 | 9 | 7 | 16 | 8.19% | 20.48%
2024-09-07 17:00 | 9 | 7 | 17 | 3.677% | 23.64%
2024-09-07 18:00 | 9 | 7 | 18 | 0.2789% | 24.7%
2024-09-07 19:00 | 9 | 7 | 19 | 0% | 27.35%
2024-09-07 20:00 | 9 | 7 | 20 | 0% | 28.97%
2024-09-07 21:00 | 9 | 7 | 21 | 0% | 29.67%
2024-09-07 22:00 | 9 | 7 | 22 | 0% | 29.39%
2024-09-07 23:00 | 9 | 7 | 23 | 0% | 28.45%
2024-09-08 | 9 | 8 | 0 | 0% | 27.01%
2024-09-08 01:00 | 9 | 8 | 1 | 0% | 27.07%
2024-09-08 02:00 | 9 | 8 | 2 | 0% | 26.37%
2024-09-08 03:00 | 9 | 8 | 3 | 0% | 25.87%
2024-09-08 04:00 | 9 | 8 | 4 | 0% | 25.3%
2024-09-08 05:00 | 9 | 8 | 5 | 0% | 24.94%
2024-09-08 06:00 | 9 | 8 | 6 | 1.311% | 23.45%
2024-09-08 07:00 | 9 | 8 | 7 | 5.712% | 21.58%
2024-09-08 08:00 | 9 | 8 | 8 | 10.79% | 20.28%
2024-09-08 09:00 | 9 | 8 | 9 | 15.06% | 19.68%
2024-09-08 10:00 | 9 | 8 | 10 | 22.46% | 19.61%
2024-09-08 11:00 | 9 | 8 | 11 | 26.27% | 19.91%
2024-09-08 12:00 | 9 | 8 | 12 | 37.07% | 20.47%
2024-09-08 13:00 | 9 | 8 | 13 | 44.26% | 22.73%
2024-09-08 14:00 | 9 | 8 | 14 | 51.51% | 22.87%
2024-09-08 15:00 | 9 | 8 | 15 | 32.87% | 20.71%
2024-09-08 16:00 | 9 | 8 | 16 | 13.66% | 20.57%
2024-09-08 17:00 | 9 | 8 | 17 | 6.389% | 20.94%
2024-09-08 18:00 | 9 | 8 | 18 | 0.5456% | 22.99%
2024-09-08 19:00 | 9 | 8 | 19 | 0% | 25.38%
2024-09-08 20:00 | 9 | 8 | 20 | 0% | 27.14%
2024-09-08 21:00 | 9 | 8 | 21 | 0% | 28.47%
2024-09-08 22:00 | 9 | 8 | 22 | 0% | 28.69%
2024-09-08 23:00 | 9 | 8 | 23 | 0% | 28.35%
2024-09-09 | 9 | 9 | 0 | 0% | 26.96%
2024-09-09 01:00 | 9 | 9 | 1 | 0% | 26.31%
2024-09-09 02:00 | 9 | 9 | 2 | 0% | 25.77%
2024-09-09 03:00 | 9 | 9 | 3 | 0% | 25.37%
2024-09-09 04:00 | 9 | 9 | 4 | 0% | 25.8%
2024-09-09 05:00 | 9 | 9 | 5 | 0% | 24.88%
2024-09-09 06:00 | 9 | 9 | 6 | 2.192% | 24.55%
2024-09-09 07:00 | 9 | 9 | 7 | 3.248% | 22.81%
2024-09-09 08:00 | 9 | 9 | 8 | 7.573% | 21.56%
2024-09-09 09:00 | 9 | 9 | 9 | 11.48% | 21.39%
2024-09-09 10:00 | 9 | 9 | 10 | 11.24% | 22.22%
2024-09-09 11:00 | 9 | 9 | 11 | 15.18% | 22.77%
2024-09-09 12:00 | 9 | 9 | 12 | 28.34% | 22.89%
2024-09-09 13:00 | 9 | 9 | 13 | 43.51% | 22.94%
2024-09-09 14:00 | 9 | 9 | 14 | 46.92% | 22.49%
2024-09-09 15:00 | 9 | 9 | 15 | 47.47% | 21.66%
2024-09-09 16:00 | 9 | 9 | 16 | 28.05% | 21.43%
2024-09-09 17:00 | 9 | 9 | 17 | 8.172% | 21.98%
2024-09-09 18:00 | 9 | 9 | 18 | 0.3879% | 23.61%
2024-09-09 19:00 | 9 | 9 | 19 | 0% | 25.81%
2024-09-09 20:00 | 9 | 9 | 20 | 0% | 27.1%
2024-09-09 21:00 | 9 | 9 | 21 | 0% | 27.85%
2024-09-09 22:00 | 9 | 9 | 22 | 0% | 27.9%
2024-09-09 23:00 | 9 | 9 | 23 | 0% | 27.42%
2024-09-10 | 9 | 10 | 0 | 0% | 24.82%
2024-09-10 01:00 | 9 | 10 | 1 | 0% | 26.61%
2024-09-10 02:00 | 9 | 10 | 2 | 0% | 27.1%
2024-09-10 03:00 | 9 | 10 | 3 | 0% | 27.69%
2024-09-10 04:00 | 9 | 10 | 4 | 0% | 30.58%
2024-09-10 05:00 | 9 | 10 | 5 | 0% | 28.61%
2024-09-10 06:00 | 9 | 10 | 6 | 4.26% | 28.14%
2024-09-10 07:00 | 9 | 10 | 7 | 17.48% | 26.15%
2024-09-10 08:00 | 9 | 10 | 8 | 19.49% | 26.6%
2024-09-10 09:00 | 9 | 10 | 9 | 32.89% | 25.36%
2024-09-10 10:00 | 9 | 10 | 10 | 70.08% | 25.75%
2024-09-10 11:00 | 9 | 10 | 11 | 75.41% | 26.08%
2024-09-10 12:00 | 9 | 10 | 12 | 75.41% | 26.28%
2024-09-10 13:00 | 9 | 10 | 13 | 70.92% | 25.8%
2024-09-10 14:00 | 9 | 10 | 14 | 61.38% | 25.58%
2024-09-10 15:00 | 9 | 10 | 15 | 46.06% | 25.52%
2024-09-10 16:00 | 9 | 10 | 16 | 20.61% | 24.56%
2024-09-10 17:00 | 9 | 10 | 17 | 5.391% | 24.32%
2024-09-10 18:00 | 9 | 10 | 18 | 0.3572% | 25.36%
2024-09-10 19:00 | 9 | 10 | 19 | 0% | 26.57%
2024-09-10 20:00 | 9 | 10 | 20 | 0% | 27.28%
2024-09-10 21:00 | 9 | 10 | 21 | 0% | 28.02%
2024-09-10 22:00 | 9 | 10 | 22 | 0% | 26.79%
2024-09-10 23:00 | 9 | 10 | 23 | 0% | 25.79%
2024-09-11 | 9 | 11 | 0 | 0% | 36.23%
2024-09-11 01:00 | 9 | 11 | 1 | 0% | 23.62%
2024-09-11 02:00 | 9 | 11 | 2 | 0% | 22.99%
2024-09-11 03:00 | 9 | 11 | 3 | 0% | 22.69%
2024-09-11 04:00 | 9 | 11 | 4 | 0% | 23.08%
2024-09-11 05:00 | 9 | 11 | 5 | 0% | 22.57%
2024-09-11 06:00 | 9 | 11 | 6 | 3.584% | 23.37%
2024-09-11 07:00 | 9 | 11 | 7 | 7.655% | 22.82%
2024-09-11 08:00 | 9 | 11 | 8 | 6.457% | 22.96%
2024-09-11 09:00 | 9 | 11 | 9 | 16.86% | 26.37%
2024-09-11 10:00 | 9 | 11 | 10 | 22.38% | 25.37%
2024-09-11 11:00 | 9 | 11 | 11 | 14.82% | 26.27%
2024-09-11 12:00 | 9 | 11 | 12 | 18.54% | 27.71%
2024-09-11 13:00 | 9 | 11 | 13 | 45.33% | 28.79%
2024-09-11 14:00 | 9 | 11 | 14 | 54.26% | 30.09%
2024-09-11 15:00 | 9 | 11 | 15 | 48% | 31.53%
2024-09-11 16:00 | 9 | 11 | 16 | 27.45% | 32.28%
2024-09-11 17:00 | 9 | 11 | 17 | 7.495% | 32.99%
2024-09-11 18:00 | 9 | 11 | 18 | 0% | 34.86%
2024-09-11 19:00 | 9 | 11 | 19 | 0% | 36.96%
2024-09-11 20:00 | 9 | 11 | 20 | 0% | 38.08%
2024-09-11 21:00 | 9 | 11 | 21 | 0% | 38.25%
2024-09-11 22:00 | 9 | 11 | 22 | 0% | 37.79%
2024-09-11 23:00 | 9 | 11 | 23 | 0% | 37.16%
2024-09-12 | 9 | 12 | 0 | 0% | 40.93%
2024-09-12 01:00 | 9 | 12 | 1 | 0% | 35.48%
2024-09-12 02:00 | 9 | 12 | 2 | 0% | 36.02%
2024-09-12 03:00 | 9 | 12 | 3 | 0% | 34.09%
2024-09-12 04:00 | 9 | 12 | 4 | 0% | 33.39%
2024-09-12 05:00 | 9 | 12 | 5 | 0% | 33%
2024-09-12 06:00 | 9 | 12 | 6 | 4.396% | 32.63%
2024-09-12 07:00 | 9 | 12 | 7 | 12.57% | 31.51%
2024-09-12 08:00 | 9 | 12 | 8 | 13.28% | 31.29%
2024-09-12 09:00 | 9 | 12 | 9 | 48.71% | 32.57%
2024-09-12 10:00 | 9 | 12 | 10 | 59.7% | 34.07%
2024-09-12 11:00 | 9 | 12 | 11 | 56.3% | 35.59%
2024-09-12 12:00 | 9 | 12 | 12 | 47.85% | 36.27%
2024-09-12 13:00 | 9 | 12 | 13 | 29.52% | 36.64%
2024-09-12 14:00 | 9 | 12 | 14 | 35.19% | 37.11%
2024-09-12 15:00 | 9 | 12 | 15 | 44.14% | 37.66%
2024-09-12 16:00 | 9 | 12 | 16 | 24.89% | 37.22%
2024-09-12 17:00 | 9 | 12 | 17 | 6.555% | 36.99%
2024-09-12 18:00 | 9 | 12 | 18 | 0% | 38.36%
2024-09-12 19:00 | 9 | 12 | 19 | 0% | 39.81%
2024-09-12 20:00 | 9 | 12 | 20 | 0% | 41.45%
2024-09-12 21:00 | 9 | 12 | 21 | 0% | 42.17%
2024-09-12 22:00 | 9 | 12 | 22 | 0% | 41.83%
2024-09-12 23:00 | 9 | 12 | 23 | 0% | 41.39%
2024-09-13 | 9 | 13 | 0 | 0% | 29.67%
2024-09-13 01:00 | 9 | 13 | 1 | 0% | 40.06%
2024-09-13 02:00 | 9 | 13 | 2 | 0% | 38.79%
2024-09-13 03:00 | 9 | 13 | 3 | 0% | 37.49%
2024-09-13 04:00 | 9 | 13 | 4 | 0% | 36.33%
2024-09-13 05:00 | 9 | 13 | 5 | 0% | 35.08%
2024-09-13 06:00 | 9 | 13 | 6 | 3.03% | 33.56%
2024-09-13 07:00 | 9 | 13 | 7 | 14.58% | 31.22%
2024-09-13 08:00 | 9 | 13 | 8 | 28.87% | 29.66%
2024-09-13 09:00 | 9 | 13 | 9 | 21.8% | 28.93%
2024-09-13 10:00 | 9 | 13 | 10 | 49.77% | 28.82%
2024-09-13 11:00 | 9 | 13 | 11 | 24.71% | 28.81%
2024-09-13 12:00 | 9 | 13 | 12 | 68.79% | 28.78%
2024-09-13 13:00 | 9 | 13 | 13 | 62.68% | 28.29%
2024-09-13 14:00 | 9 | 13 | 14 | 43.27% | 30.47%
2024-09-13 15:00 | 9 | 13 | 15 | 31.78% | 27.47%
2024-09-13 16:00 | 9 | 13 | 16 | 15.92% | 26.44%
2024-09-13 17:00 | 9 | 13 | 17 | 3.912% | 25.92%
2024-09-13 18:00 | 9 | 13 | 18 | 0% | 26.97%
2024-09-13 19:00 | 9 | 13 | 19 | 0% | 28.92%
2024-09-13 20:00 | 9 | 13 | 20 | 0% | 30.52%
2024-09-13 21:00 | 9 | 13 | 21 | 0% | 31.43%
2024-09-13 22:00 | 9 | 13 | 22 | 0% | 31.05%
2024-09-13 23:00 | 9 | 13 | 23 | 0% | 27.98%
2024-09-14 | 9 | 14 | 0 | 0% | 27.4%
2024-09-14 01:00 | 9 | 14 | 1 | 0% | 29.41%
2024-09-14 02:00 | 9 | 14 | 2 | 0% | 29.07%
2024-09-14 03:00 | 9 | 14 | 3 | 0% | 28.8%
2024-09-14 04:00 | 9 | 14 | 4 | 0% | 28.25%
2024-09-14 05:00 | 9 | 14 | 5 | 0% | 27.48%
2024-09-14 06:00 | 9 | 14 | 6 | 0.874% | 26.31%
2024-09-14 07:00 | 9 | 14 | 7 | 2.965% | 23.76%
2024-09-14 08:00 | 9 | 14 | 8 | 9.075% | 21.88%
2024-09-14 09:00 | 9 | 14 | 9 | 8.478% | 21.11%
2024-09-14 10:00 | 9 | 14 | 10 | 25.97% | 21.01%
2024-09-14 11:00 | 9 | 14 | 11 | 45.72% | 21.48%
2024-09-14 12:00 | 9 | 14 | 12 | 54.28% | 22.15%
2024-09-14 13:00 | 9 | 14 | 13 | 48.2% | 22.72%
2024-09-14 14:00 | 9 | 14 | 14 | 45% | 22.88%
2024-09-14 15:00 | 9 | 14 | 15 | 26.01% | 23.14%
2024-09-14 16:00 | 9 | 14 | 16 | 11.73% | 22.94%
2024-09-14 17:00 | 9 | 14 | 17 | 4.009% | 23.13%
2024-09-14 18:00 | 9 | 14 | 18 | 0% | 24.12%
2024-09-14 19:00 | 9 | 14 | 19 | 0% | 25.29%
2024-09-14 20:00 | 9 | 14 | 20 | 0% | 26.33%
2024-09-14 21:00 | 9 | 14 | 21 | 0% | 26.73%
2024-09-14 22:00 | 9 | 14 | 22 | 0% | 27.16%
2024-09-14 23:00 | 9 | 14 | 23 | 0% | 27.33%
2024-09-15 | 9 | 15 | 0 | 0% | 33.78%
2024-09-15 01:00 | 9 | 15 | 1 | 0% | 27.25%
2024-09-15 02:00 | 9 | 15 | 2 | 0% | 26.92%
2024-09-15 03:00 | 9 | 15 | 3 | 0% | 26.59%
2024-09-15 04:00 | 9 | 15 | 4 | 0% | 25.98%
2024-09-15 05:00 | 9 | 15 | 5 | 0% | 25.43%
2024-09-15 06:00 | 9 | 15 | 6 | 2.17% | 24.45%
2024-09-15 07:00 | 9 | 15 | 7 | 12.95% | 22.6%
2024-09-15 08:00 | 9 | 15 | 8 | 37.57% | 21.61%
2024-09-15 09:00 | 9 | 15 | 9 | 53.82% | 21.94%
2024-09-15 10:00 | 9 | 15 | 10 | 54.08% | 23.46%
2024-09-15 11:00 | 9 | 15 | 11 | 71.5% | 25.05%
2024-09-15 12:00 | 9 | 15 | 12 | 71.85% | 26.03%
2024-09-15 13:00 | 9 | 15 | 13 | 66.02% | 27.28%
2024-09-15 14:00 | 9 | 15 | 14 | 56.13% | 27.89%
2024-09-15 15:00 | 9 | 15 | 15 | 41.3% | 30.35%
2024-09-15 16:00 | 9 | 15 | 16 | 22.32% | 22.92%
2024-09-15 17:00 | 9 | 15 | 17 | 4.317% | 28%
2024-09-15 18:00 | 9 | 15 | 18 | 0% | 29.18%
2024-09-15 19:00 | 9 | 15 | 19 | 0% | 30.92%
2024-09-15 20:00 | 9 | 15 | 20 | 0% | 32.58%
2024-09-15 21:00 | 9 | 15 | 21 | 0% | 33.84%
2024-09-15 22:00 | 9 | 15 | 22 | 0% | 34.04%
2024-09-15 23:00 | 9 | 15 | 23 | 0% | 34.4%
2024-09-16 | 9 | 16 | 0 | 0% | 36.83%
2024-09-16 01:00 | 9 | 16 | 1 | 0% | 33.97%
2024-09-16 02:00 | 9 | 16 | 2 | 0% | 34.45%
2024-09-16 03:00 | 9 | 16 | 3 | 0% | 34.8%
2024-09-16 04:00 | 9 | 16 | 4 | 0% | 34.75%
2024-09-16 05:00 | 9 | 16 | 5 | 0% | 34.58%
2024-09-16 06:00 | 9 | 16 | 6 | 1.966% | 33.51%
2024-09-16 07:00 | 9 | 16 | 7 | 6.823% | 31.38%
2024-09-16 08:00 | 9 | 16 | 8 | 24.54% | 30.16%
2024-09-16 09:00 | 9 | 16 | 9 | 45.98% | 29.38%
2024-09-16 10:00 | 9 | 16 | 10 | 42.97% | 26.7%
2024-09-16 11:00 | 9 | 16 | 11 | 48.12% | 29.13%
2024-09-16 12:00 | 9 | 16 | 12 | 60.5% | 28.71%
2024-09-16 13:00 | 9 | 16 | 13 | 29.53% | 28.45%
2024-09-16 14:00 | 9 | 16 | 14 | 14.76% | 28.7%
2024-09-16 15:00 | 9 | 16 | 15 | 12.69% | 28.77%
2024-09-16 16:00 | 9 | 16 | 16 | 8.259% | 29.32%
2024-09-16 17:00 | 9 | 16 | 17 | 3.424% | 30.56%
2024-09-16 18:00 | 9 | 16 | 18 | 0% | 32.73%
2024-09-16 19:00 | 9 | 16 | 19 | 0% | 34.71%
2024-09-16 20:00 | 9 | 16 | 20 | 0% | 36.07%
2024-09-16 21:00 | 9 | 16 | 21 | 0% | 36.59%
2024-09-16 22:00 | 9 | 16 | 22 | 0% | 36.76%
2024-09-16 23:00 | 9 | 16 | 23 | 0% | 36.97%
2024-09-17 | 9 | 17 | 0 | 0% | 28.58%
2024-09-17 01:00 | 9 | 17 | 1 | 0% | 36.69%
2024-09-17 02:00 | 9 | 17 | 2 | 0% | 34.36%
2024-09-17 03:00 | 9 | 17 | 3 | 0% | 36.15%
2024-09-17 04:00 | 9 | 17 | 4 | 0% | 35.75%
2024-09-17 05:00 | 9 | 17 | 5 | 0% | 35.68%
2024-09-17 06:00 | 9 | 17 | 6 | 4.083% | 34.92%
2024-09-17 07:00 | 9 | 17 | 7 | 22.14% | 32.51%
2024-09-17 08:00 | 9 | 17 | 8 | 42.81% | 30.24%
2024-09-17 09:00 | 9 | 17 | 9 | 59.44% | 28.46%
2024-09-17 10:00 | 9 | 17 | 10 | 70.55% | 26.64%
2024-09-17 11:00 | 9 | 17 | 11 | 60.32% | 25.34%
2024-09-17 12:00 | 9 | 17 | 12 | 61.67% | 24.72%
2024-09-17 13:00 | 9 | 17 | 13 | 49.04% | 24.17%
2024-09-17 14:00 | 9 | 17 | 14 | 38.51% | 23.64%
2024-09-17 15:00 | 9 | 17 | 15 | 31.7% | 23.28%
2024-09-17 16:00 | 9 | 17 | 16 | 19.26% | 20.87%
2024-09-17 17:00 | 9 | 17 | 17 | 4.096% | 22.35%
2024-09-17 18:00 | 9 | 17 | 18 | 0% | 23.21%
2024-09-17 19:00 | 9 | 17 | 19 | 0% | 24.79%
2024-09-17 20:00 | 9 | 17 | 20 | 0% | 26.03%
2024-09-17 21:00 | 9 | 17 | 21 | 0% | 27.06%
2024-09-17 22:00 | 9 | 17 | 22 | 0% | 26.72%
2024-09-17 23:00 | 9 | 17 | 23 | 0% | 26.9%
2024-09-18 | 9 | 18 | 0 | 0% | 34.41%
2024-09-18 01:00 | 9 | 18 | 1 | 0% | 26.66%
2024-09-18 02:00 | 9 | 18 | 2 | 0% | 26.76%
2024-09-18 03:00 | 9 | 18 | 3 | 0% | 27.17%
2024-09-18 04:00 | 9 | 18 | 4 | 0% | 27.43%
2024-09-18 05:00 | 9 | 18 | 5 | 0% | 28.04%
2024-09-18 06:00 | 9 | 18 | 6 | 1.333% | 27.91%
2024-09-18 07:00 | 9 | 18 | 7 | 4.333% | 26.37%
2024-09-18 08:00 | 9 | 18 | 8 | 12.89% | 25.11%
2024-09-18 09:00 | 9 | 18 | 9 | 24.15% | 24.82%
2024-09-18 10:00 | 9 | 18 | 10 | 47.45% | 25.63%
2024-09-18 11:00 | 9 | 18 | 11 | 24.5% | 26.72%
2024-09-18 12:00 | 9 | 18 | 12 | 33.48% | 28.46%
2024-09-18 13:00 | 9 | 18 | 13 | 35.5% | 29.8%
2024-09-18 14:00 | 9 | 18 | 14 | 28.39% | 30.27%
2024-09-18 15:00 | 9 | 18 | 15 | 16.77% | 32.22%
2024-09-18 16:00 | 9 | 18 | 16 | 10.49% | 32.69%
2024-09-18 17:00 | 9 | 18 | 17 | 2.736% | 33.8%
2024-09-18 18:00 | 9 | 18 | 18 | 0% | 35.53%
2024-09-18 19:00 | 9 | 18 | 19 | 0% | 36.82%
2024-09-18 20:00 | 9 | 18 | 20 | 0% | 37.28%
2024-09-18 21:00 | 9 | 18 | 21 | 0% | 37.09%
2024-09-18 22:00 | 9 | 18 | 22 | 0% | 36.05%
2024-09-18 23:00 | 9 | 18 | 23 | 0% | 38.81%
2024-09-19 | 9 | 19 | 0 | 0% | 32.81%
2024-09-19 01:00 | 9 | 19 | 1 | 0% | 33.74%
2024-09-19 02:00 | 9 | 19 | 2 | 0% | 33.21%
2024-09-19 03:00 | 9 | 19 | 3 | 0% | 33.16%
2024-09-19 04:00 | 9 | 19 | 4 | 0% | 33.28%
2024-09-19 05:00 | 9 | 19 | 5 | 0% | 33.41%
2024-09-19 06:00 | 9 | 19 | 6 | 0.6272% | 32.85%
2024-09-19 07:00 | 9 | 19 | 7 | 4.504% | 31.42%
2024-09-19 08:00 | 9 | 19 | 8 | 9.752% | 30.78%
2024-09-19 09:00 | 9 | 19 | 9 | 16.43% | 30.86%
2024-09-19 10:00 | 9 | 19 | 10 | 15.4% | 30.64%
2024-09-19 11:00 | 9 | 19 | 11 | 11.71% | 30.26%
2024-09-19 12:00 | 9 | 19 | 12 | 10.56% | 30.25%
2024-09-19 13:00 | 9 | 19 | 13 | 13.67% | 30.32%
2024-09-19 14:00 | 9 | 19 | 14 | 11.52% | 30.29%
2024-09-19 15:00 | 9 | 19 | 15 | 9.258% | 30.04%
2024-09-19 16:00 | 9 | 19 | 16 | 5.346% | 29.43%
2024-09-19 17:00 | 9 | 19 | 17 | 2.185% | 29.38%
2024-09-19 18:00 | 9 | 19 | 18 | 0% | 30.5%
2024-09-19 19:00 | 9 | 19 | 19 | 0% | 31.31%
2024-09-19 20:00 | 9 | 19 | 20 | 0% | 31.76%
2024-09-19 21:00 | 9 | 19 | 21 | 0% | 33.87%
2024-09-19 22:00 | 9 | 19 | 22 | 0% | 32.42%
2024-09-19 23:00 | 9 | 19 | 23 | 0% | 32.18%
2024-09-20 | 9 | 20 | 0 | 0% | 25.72%
2024-09-20 01:00 | 9 | 20 | 1 | 0% | 32.84%
2024-09-20 02:00 | 9 | 20 | 2 | 0% | 32.95%
2024-09-20 03:00 | 9 | 20 | 3 | 0% | 32.91%
2024-09-20 04:00 | 9 | 20 | 4 | 0% | 32.08%
2024-09-20 05:00 | 9 | 20 | 5 | 0% | 30.9%
2024-09-20 06:00 | 9 | 20 | 6 | 0.7193% | 29.34%
2024-09-20 07:00 | 9 | 20 | 7 | 3.793% | 26.79%
2024-09-20 08:00 | 9 | 20 | 8 | 7.66% | 24.69%
2024-09-20 09:00 | 9 | 20 | 9 | 10.57% | 23.52%
2024-09-20 10:00 | 9 | 20 | 10 | 8.03% | 22.73%
2024-09-20 11:00 | 9 | 20 | 11 | 14.96% | 22.13%
2024-09-20 12:00 | 9 | 20 | 12 | 26.23% | 22.08%
2024-09-20 13:00 | 9 | 20 | 13 | 28.29% | 22.11%
2024-09-20 14:00 | 9 | 20 | 14 | 15.58% | 22.67%
2024-09-20 15:00 | 9 | 20 | 15 | 13.96% | 22.73%
2024-09-20 16:00 | 9 | 20 | 16 | 8.502% | 22.74%
2024-09-20 17:00 | 9 | 20 | 17 | 0.9449% | 23.33%
2024-09-20 18:00 | 9 | 20 | 18 | 0% | 25.34%
2024-09-20 19:00 | 9 | 20 | 19 | 0% | 26.83%
2024-09-20 20:00 | 9 | 20 | 20 | 0% | 27.27%
2024-09-20 21:00 | 9 | 20 | 21 | 0% | 27.15%
2024-09-20 22:00 | 9 | 20 | 22 | 0% | 26.42%
2024-09-20 23:00 | 9 | 20 | 23 | 0% | 25.84%
2024-09-21 | 9 | 21 | 0 | 0% | 30.04%
2024-09-21 01:00 | 9 | 21 | 1 | 0% | 25.09%
2024-09-21 02:00 | 9 | 21 | 2 | 0% | 24.65%
2024-09-21 03:00 | 9 | 21 | 3 | 0% | 24.86%
2024-09-21 04:00 | 9 | 21 | 4 | 0% | 27.65%
2024-09-21 05:00 | 9 | 21 | 5 | 0% | 25.92%
2024-09-21 06:00 | 9 | 21 | 6 | 2.077% | 26.66%
2024-09-21 07:00 | 9 | 21 | 7 | 10.96% | 26.72%
2024-09-21 08:00 | 9 | 21 | 8 | 39.61% | 26.4%
2024-09-21 09:00 | 9 | 21 | 9 | 56.35% | 27.41%
2024-09-21 10:00 | 9 | 21 | 10 | 67.69% | 28.68%
2024-09-21 11:00 | 9 | 21 | 11 | 54.52% | 29.26%
2024-09-21 12:00 | 9 | 21 | 12 | 44.88% | 33.75%
2024-09-21 13:00 | 9 | 21 | 13 | 42.81% | 34.81%
2024-09-21 14:00 | 9 | 21 | 14 | 36.23% | 33.85%
2024-09-21 15:00 | 9 | 21 | 15 | 28.77% | 30.36%
2024-09-21 16:00 | 9 | 21 | 16 | 20.3% | 30.87%
2024-09-21 17:00 | 9 | 21 | 17 | 2.149% | 31.74%
2024-09-21 18:00 | 9 | 21 | 18 | 0% | 32.38%
2024-09-21 19:00 | 9 | 21 | 19 | 0% | 33%
2024-09-21 20:00 | 9 | 21 | 20 | 0% | 32.94%
2024-09-21 21:00 | 9 | 21 | 21 | 0% | 35.49%
2024-09-21 22:00 | 9 | 21 | 22 | 0% | 31.94%
2024-09-21 23:00 | 9 | 21 | 23 | 0% | 30.62%
2024-09-22 | 9 | 22 | 0 | 0% | 30.21%
2024-09-22 01:00 | 9 | 22 | 1 | 0% | 29.62%
2024-09-22 02:00 | 9 | 22 | 2 | 0% | 29.33%
2024-09-22 03:00 | 9 | 22 | 3 | 0% | 29.05%
2024-09-22 04:00 | 9 | 22 | 4 | 0% | 29.84%
2024-09-22 05:00 | 9 | 22 | 5 | 0% | 29.62%
2024-09-22 06:00 | 9 | 22 | 6 | 0.7235% | 28.83%
2024-09-22 07:00 | 9 | 22 | 7 | 4.744% | 29.92%
2024-09-22 08:00 | 9 | 22 | 8 | 17.38% | 26.2%
2024-09-22 09:00 | 9 | 22 | 9 | 22.85% | 25.13%
2024-09-22 10:00 | 9 | 22 | 10 | 27.84% | 25.27%
2024-09-22 11:00 | 9 | 22 | 11 | 32.69% | 25.89%
2024-09-22 12:00 | 9 | 22 | 12 | 30.71% | 26.86%
2024-09-22 13:00 | 9 | 22 | 13 | 32.29% | 27.93%
2024-09-22 14:00 | 9 | 22 | 14 | 25.44% | 28.65%
2024-09-22 15:00 | 9 | 22 | 15 | 11.63% | 29.23%
2024-09-22 16:00 | 9 | 22 | 16 | 5.957% | 29.16%
2024-09-22 17:00 | 9 | 22 | 17 | 1.306% | 28.99%
2024-09-22 18:00 | 9 | 22 | 18 | 0% | 30.11%
2024-09-22 19:00 | 9 | 22 | 19 | 0% | 30.93%
2024-09-22 20:00 | 9 | 22 | 20 | 0% | 31.76%
2024-09-22 21:00 | 9 | 22 | 21 | 0% | 32.01%
2024-09-22 22:00 | 9 | 22 | 22 | 0% | 31.31%
2024-09-22 23:00 | 9 | 22 | 23 | 0% | 30.82%
2024-09-23 | 9 | 23 | 0 | 0% | 29.57%
2024-09-23 01:00 | 9 | 23 | 1 | 0% | 29.46%
2024-09-23 02:00 | 9 | 23 | 2 | 0% | 28.62%
2024-09-23 03:00 | 9 | 23 | 3 | 0% | 28.14%
2024-09-23 04:00 | 9 | 23 | 4 | 0% | 29.55%
2024-09-23 05:00 | 9 | 23 | 5 | 0% | 26.63%
2024-09-23 06:00 | 9 | 23 | 6 | 0.8009% | 26.65%
2024-09-23 07:00 | 9 | 23 | 7 | 3.512% | 23.31%
2024-09-23 08:00 | 9 | 23 | 8 | 15.63% | 21.35%
2024-09-23 09:00 | 9 | 23 | 9 | 26.49% | 20.29%
2024-09-23 10:00 | 9 | 23 | 10 | 21.37% | 19.56%
2024-09-23 11:00 | 9 | 23 | 11 | 17.52% | 19.37%
2024-09-23 12:00 | 9 | 23 | 12 | 9.723% | 20.69%
2024-09-23 13:00 | 9 | 23 | 13 | 9.798% | 19.33%
2024-09-23 14:00 | 9 | 23 | 14 | 16.1% | 19.24%
2024-09-23 15:00 | 9 | 23 | 15 | 8.081% | 18.72%
2024-09-23 16:00 | 9 | 23 | 16 | 9.228% | 19.39%
2024-09-23 17:00 | 9 | 23 | 17 | 1.984% | 20.35%
2024-09-23 18:00 | 9 | 23 | 18 | 0% | 22.53%
2024-09-23 19:00 | 9 | 23 | 19 | 0% | 25.17%
2024-09-23 20:00 | 9 | 23 | 20 | 0% | 27.48%
2024-09-23 21:00 | 9 | 23 | 21 | 0% | 29.24%
2024-09-23 22:00 | 9 | 23 | 22 | 0% | 29.46%
2024-09-23 23:00 | 9 | 23 | 23 | 0% | 29.5%
2024-09-24 | 9 | 24 | 0 | 0% | 28.63%
2024-09-24 01:00 | 9 | 24 | 1 | 0% | 29.21%
2024-09-24 02:00 | 9 | 24 | 2 | 0% | 28.66%
2024-09-24 03:00 | 9 | 24 | 3 | 0% | 28.28%
2024-09-24 04:00 | 9 | 24 | 4 | 0% | 27.93%
2024-09-24 05:00 | 9 | 24 | 5 | 0% | 27.67%
2024-09-24 06:00 | 9 | 24 | 6 | 1.83% | 27.01%
2024-09-24 07:00 | 9 | 24 | 7 | 13.04% | 25.18%
2024-09-24 08:00 | 9 | 24 | 8 | 32.24% | 23.27%
2024-09-24 09:00 | 9 | 24 | 9 | 44.33% | 21.93%
2024-09-24 10:00 | 9 | 24 | 10 | 34.68% | 21.75%
2024-09-24 11:00 | 9 | 24 | 11 | 41.93% | 22.12%
2024-09-24 12:00 | 9 | 24 | 12 | 36.99% | 23.18%
2024-09-24 13:00 | 9 | 24 | 13 | 32.39% | 23.42%
2024-09-24 14:00 | 9 | 24 | 14 | 21.65% | 23.67%
2024-09-24 15:00 | 9 | 24 | 15 | 17.55% | 23.16%
2024-09-24 16:00 | 9 | 24 | 16 | 10.17% | 23.2%
2024-09-24 17:00 | 9 | 24 | 17 | 1.464% | 23.7%
2024-09-24 18:00 | 9 | 24 | 18 | 0% | 26.23%
2024-09-24 19:00 | 9 | 24 | 19 | 0% | 28.15%
2024-09-24 20:00 | 9 | 24 | 20 | 0% | 29.97%
2024-09-24 21:00 | 9 | 24 | 21 | 0% | 30.59%
2024-09-24 22:00 | 9 | 24 | 22 | 0% | 30.11%
2024-09-24 23:00 | 9 | 24 | 23 | 0% | 29.55%
2024-09-25 | 9 | 25 | 0 | 0% | 34.98%
2024-09-25 01:00 | 9 | 25 | 1 | 0% | 28.34%
2024-09-25 02:00 | 9 | 25 | 2 | 0% | 28.46%
2024-09-25 03:00 | 9 | 25 | 3 | 0% | 28.71%
2024-09-25 04:00 | 9 | 25 | 4 | 0% | 29.21%
2024-09-25 05:00 | 9 | 25 | 5 | 0% | 30.13%
2024-09-25 06:00 | 9 | 25 | 6 | 1.306% | 30.86%
2024-09-25 07:00 | 9 | 25 | 7 | 10.08% | 30.19%
2024-09-25 08:00 | 9 | 25 | 8 | 34.86% | 29.46%
2024-09-25 09:00 | 9 | 25 | 9 | 41.12% | 29.68%
2024-09-25 10:00 | 9 | 25 | 10 | 45.08% | 30.34%
2024-09-25 11:00 | 9 | 25 | 11 | 31.34% | 31.45%
2024-09-25 12:00 | 9 | 25 | 12 | 21.45% | 32.62%
2024-09-25 13:00 | 9 | 25 | 13 | 20.38% | 33.33%
2024-09-25 14:00 | 9 | 25 | 14 | 36.04% | 34.24%
2024-09-25 15:00 | 9 | 25 | 15 | 26.87% | 34.18%
2024-09-25 16:00 | 9 | 25 | 16 | 7.529% | 34.34%
2024-09-25 17:00 | 9 | 25 | 17 | 1.028% | 35.92%
2024-09-25 18:00 | 9 | 25 | 18 | 0% | 38.07%
2024-09-25 19:00 | 9 | 25 | 19 | 0% | 39.68%
2024-09-25 20:00 | 9 | 25 | 20 | 0% | 40.42%
2024-09-25 21:00 | 9 | 25 | 21 | 0% | 39.53%
2024-09-25 22:00 | 9 | 25 | 22 | 0% | 38.39%
2024-09-25 23:00 | 9 | 25 | 23 | 0% | 36.65%
2024-09-26 | 9 | 26 | 0 | 0% | 36.44%
2024-09-26 01:00 | 9 | 26 | 1 | 0% | 33.22%
2024-09-26 02:00 | 9 | 26 | 2 | 0% | 31.55%
2024-09-26 03:00 | 9 | 26 | 3 | 0% | 29.8%
2024-09-26 04:00 | 9 | 26 | 4 | 0% | 28.73%
2024-09-26 05:00 | 9 | 26 | 5 | 0% | 27.61%
2024-09-26 06:00 | 9 | 26 | 6 | 0% | 26.29%
2024-09-26 07:00 | 9 | 26 | 7 | 2.454% | 24.04%
2024-09-26 08:00 | 9 | 26 | 8 | 11.93% | 21.62%
2024-09-26 09:00 | 9 | 26 | 9 | 25.46% | 19.84%
2024-09-26 10:00 | 9 | 26 | 10 | 21.08% | 18.83%
2024-09-26 11:00 | 9 | 26 | 11 | 18.62% | 18.75%
2024-09-26 12:00 | 9 | 26 | 12 | 34.39% | 19.12%
2024-09-26 13:00 | 9 | 26 | 13 | 23.52% | 19.59%
2024-09-26 14:00 | 9 | 26 | 14 | 18.4% | 20.24%
2024-09-26 15:00 | 9 | 26 | 15 | 6.57% | 21.57%
2024-09-26 16:00 | 9 | 26 | 16 | 2.601% | 22.43%
2024-09-26 17:00 | 9 | 26 | 17 | 0.8606% | 25.16%
2024-09-26 18:00 | 9 | 26 | 18 | 0% | 28.75%
2024-09-26 19:00 | 9 | 26 | 19 | 0% | 31.48%
2024-09-26 20:00 | 9 | 26 | 20 | 0% | 33.26%
2024-09-26 21:00 | 9 | 26 | 21 | 0% | 34.34%
2024-09-26 22:00 | 9 | 26 | 22 | 0% | 34.58%
2024-09-26 23:00 | 9 | 26 | 23 | 0% | 35.09%
2024-09-27 | 9 | 27 | 0 | 0% | 34.63%
2024-09-27 01:00 | 9 | 27 | 1 | 0% | 34.96%
2024-09-27 02:00 | 9 | 27 | 2 | 0% | 34.47%
2024-09-27 03:00 | 9 | 27 | 3 | 0% | 35.45%
2024-09-27 04:00 | 9 | 27 | 4 | 0% | 34.46%
2024-09-27 05:00 | 9 | 27 | 5 | 0% | 34.62%
2024-09-27 06:00 | 9 | 27 | 6 | 0.3622% | 34.02%
2024-09-27 07:00 | 9 | 27 | 7 | 1.629% | 32.74%
2024-09-27 08:00 | 9 | 27 | 8 | 5.27% | 31.03%
2024-09-27 09:00 | 9 | 27 | 9 | 8.929% | 29.76%
2024-09-27 10:00 | 9 | 27 | 10 | 8.813% | 28.92%
2024-09-27 11:00 | 9 | 27 | 11 | 22.76% | 29.11%
2024-09-27 12:00 | 9 | 27 | 12 | 29.38% | 29.91%
2024-09-27 13:00 | 9 | 27 | 13 | 31.03% | 30.88%
2024-09-27 14:00 | 9 | 27 | 14 | 15.98% | 32.19%
2024-09-27 15:00 | 9 | 27 | 15 | 20.59% | 33.17%
2024-09-27 16:00 | 9 | 27 | 16 | 5.577% | 33.06%
2024-09-27 17:00 | 9 | 27 | 17 | 0.7839% | 34.32%
2024-09-27 18:00 | 9 | 27 | 18 | 0% | 36.57%
2024-09-27 19:00 | 9 | 27 | 19 | 0% | 37.89%
2024-09-27 20:00 | 9 | 27 | 20 | 0% | 38.29%
2024-09-27 21:00 | 9 | 27 | 21 | 0% | 37.28%
2024-09-27 22:00 | 9 | 27 | 22 | 0% | 36.21%
2024-09-27 23:00 | 9 | 27 | 23 | 0% | 35.55%
2024-09-28 | 9 | 28 | 0 | 0% | 28.58%
2024-09-28 01:00 | 9 | 28 | 1 | 0% | 34.12%
2024-09-28 02:00 | 9 | 28 | 2 | 0% | 33.77%
2024-09-28 03:00 | 9 | 28 | 3 | 0% | 33.75%
2024-09-28 04:00 | 9 | 28 | 4 | 0% | 33.94%
2024-09-28 05:00 | 9 | 28 | 5 | 0% | 33.98%
2024-09-28 06:00 | 9 | 28 | 6 | 0.3515% | 34.44%
2024-09-28 07:00 | 9 | 28 | 7 | 3.405% | 32.82%
2024-09-28 08:00 | 9 | 28 | 8 | 4.959% | 30.95%
2024-09-28 09:00 | 9 | 28 | 9 | 29.59% | 29.79%
2024-09-28 10:00 | 9 | 28 | 10 | 22.2% | 29.67%
2024-09-28 11:00 | 9 | 28 | 11 | 47.29% | 29.84%
2024-09-28 12:00 | 9 | 28 | 12 | 19.61% | 29.81%
2024-09-28 13:00 | 9 | 28 | 13 | 19.52% | 29.97%
2024-09-28 14:00 | 9 | 28 | 14 | 13.4% | 29.88%
2024-09-28 15:00 | 9 | 28 | 15 | 6.162% | 29.33%
2024-09-28 16:00 | 9 | 28 | 16 | 3.106% | 28.86%
2024-09-28 17:00 | 9 | 28 | 17 | 0.3559% | 28.65%
2024-09-28 18:00 | 9 | 28 | 18 | 0% | 31.45%
2024-09-28 19:00 | 9 | 28 | 19 | 0% | 32.28%
2024-09-28 20:00 | 9 | 28 | 20 | 0% | 32.15%
2024-09-28 21:00 | 9 | 28 | 21 | 0% | 31.7%
2024-09-28 22:00 | 9 | 28 | 22 | 0% | 30.74%
2024-09-28 23:00 | 9 | 28 | 23 | 0% | 29.44%
2024-09-29 | 9 | 29 | 0 | 0% | 34.42%
2024-09-29 01:00 | 9 | 29 | 1 | 0% | 27.31%
2024-09-29 02:00 | 9 | 29 | 2 | 0% | 26.67%
2024-09-29 03:00 | 9 | 29 | 3 | 0% | 26.75%
2024-09-29 04:00 | 9 | 29 | 4 | 0% | 28.21%
2024-09-29 05:00 | 9 | 29 | 5 | 0% | 29.35%
2024-09-29 06:00 | 9 | 29 | 6 | 0% | 30.12%
2024-09-29 07:00 | 9 | 29 | 7 | 0.7952% | 30.18%
2024-09-29 08:00 | 9 | 29 | 8 | 3.182% | 29.47%
2024-09-29 09:00 | 9 | 29 | 9 | 5.129% | 28.8%
2024-09-29 10:00 | 9 | 29 | 10 | 5.91% | 29.05%
2024-09-29 11:00 | 9 | 29 | 11 | 6.262% | 29.66%
2024-09-29 12:00 | 9 | 29 | 12 | 3.971% | 26.59%
2024-09-29 13:00 | 9 | 29 | 13 | 7.759% | 30.13%
2024-09-29 14:00 | 9 | 29 | 14 | 8.308% | 30.2%
2024-09-29 15:00 | 9 | 29 | 15 | 6.638% | 29.69%
2024-09-29 16:00 | 9 | 29 | 16 | 4.85% | 29.46%
2024-09-29 17:00 | 9 | 29 | 17 | 0.871% | 30.57%
2024-09-29 18:00 | 9 | 29 | 18 | 0% | 29.16%
2024-09-29 19:00 | 9 | 29 | 19 | 0% | 33.72%
2024-09-29 20:00 | 9 | 29 | 20 | 0% | 34.76%
2024-09-29 21:00 | 9 | 29 | 21 | 0% | 35.19%
2024-09-29 22:00 | 9 | 29 | 22 | 0% | 35.02%
2024-09-29 23:00 | 9 | 29 | 23 | 0% | 34.46%
2024-09-30 | 9 | 30 | 0 | 0% | 37.25%
2024-09-30 01:00 | 9 | 30 | 1 | 0% | 34.23%
2024-09-30 02:00 | 9 | 30 | 2 | 0% | 33.96%
2024-09-30 03:00 | 9 | 30 | 3 | 0% | 33.46%
2024-09-30 04:00 | 9 | 30 | 4 | 0% | 33.64%
2024-09-30 05:00 | 9 | 30 | 5 | 0% | 33.52%
2024-09-30 06:00 | 9 | 30 | 6 | 0.846% | 33.37%
2024-09-30 07:00 | 9 | 30 | 7 | 5.4% | 32.42%
2024-09-30 08:00 | 9 | 30 | 8 | 10.58% | 31.77%
2024-09-30 09:00 | 9 | 30 | 9 | 12.14% | 31.11%
2024-09-30 10:00 | 9 | 30 | 10 | 16.21% | 30.33%
2024-09-30 11:00 | 9 | 30 | 11 | 31.84% | 30.19%
2024-09-30 12:00 | 9 | 30 | 12 | 28.11% | 30.08%
2024-09-30 13:00 | 9 | 30 | 13 | 18.6% | 32.56%
2024-09-30 14:00 | 9 | 30 | 14 | 17.93% | 30.29%
2024-09-30 15:00 | 9 | 30 | 15 | 11.18% | 30.38%
2024-09-30 16:00 | 9 | 30 | 16 | 3.977% | 30.67%
2024-09-30 17:00 | 9 | 30 | 17 | 0.7961% | 32.82%
2024-09-30 18:00 | 9 | 30 | 18 | 0% | 35.2%
2024-09-30 19:00 | 9 | 30 | 19 | 0% | 36.94%
2024-09-30 20:00 | 9 | 30 | 20 | 0% | 38.13%
2024-09-30 21:00 | 9 | 30 | 21 | 0% | 38.39%
2024-09-30 22:00 | 9 | 30 | 22 | 0% | 38.15%
2024-09-30 23:00 | 9 | 30 | 23 | 0% | 37.93%
2024-10-01 | 10 | 1 | 0 | 0% | 29.07%
2024-10-01 01:00 | 10 | 1 | 1 | 0% | 36.39%
2024-10-01 02:00 | 10 | 1 | 2 | 0% | 37.55%
2024-10-01 03:00 | 10 | 1 | 3 | 0% | 34.97%
2024-10-01 04:00 | 10 | 1 | 4 | 0% | 34.75%
2024-10-01 05:00 | 10 | 1 | 5 | 0% | 35.01%
2024-10-01 06:00 | 10 | 1 | 6 | 0.3609% | 34.72%
2024-10-01 07:00 | 10 | 1 | 7 | 5.88% | 33.24%
2024-10-01 08:00 | 10 | 1 | 8 | 10.14% | 31.18%
2024-10-01 09:00 | 10 | 1 | 9 | 29.2% | 29.79%
2024-10-01 10:00 | 10 | 1 | 10 | 18.36% | 29.07%
2024-10-01 11:00 | 10 | 1 | 11 | 12.84% | 28.89%
2024-10-01 12:00 | 10 | 1 | 12 | 3.729% | 28.97%
2024-10-01 13:00 | 10 | 1 | 13 | 5.052% | 28.78%
2024-10-01 14:00 | 10 | 1 | 14 | 5.721% | 28.15%
2024-10-01 15:00 | 10 | 1 | 15 | 2.655% | 27.95%
2024-10-01 16:00 | 10 | 1 | 16 | 2.079% | 27.81%
2024-10-01 17:00 | 10 | 1 | 17 | 0.274% | 29.26%
2024-10-01 18:00 | 10 | 1 | 18 | 0% | 30.92%
2024-10-01 19:00 | 10 | 1 | 19 | 0% | 32.42%
2024-10-01 20:00 | 10 | 1 | 20 | 0% | 32.71%
2024-10-01 21:00 | 10 | 1 | 21 | 0% | 32.1%
2024-10-01 22:00 | 10 | 1 | 22 | 0% | 30.95%
2024-10-01 23:00 | 10 | 1 | 23 | 0% | 29.74%
2024-10-02 | 10 | 2 | 0 | 0% | 34.39%
2024-10-02 01:00 | 10 | 2 | 1 | 0% | 31.25%
2024-10-02 02:00 | 10 | 2 | 2 | 0% | 29.4%
2024-10-02 03:00 | 10 | 2 | 3 | 0% | 30.43%
2024-10-02 04:00 | 10 | 2 | 4 | 0% | 31.39%
2024-10-02 05:00 | 10 | 2 | 5 | 0% | 32.42%
2024-10-02 06:00 | 10 | 2 | 6 | 0% | 33.46%
2024-10-02 07:00 | 10 | 2 | 7 | 0.3866% | 33.06%
2024-10-02 08:00 | 10 | 2 | 8 | 1.589% | 32.43%
2024-10-02 09:00 | 10 | 2 | 9 | 4.958% | 31.66%
2024-10-02 10:00 | 10 | 2 | 10 | 1.672% | 31.7%
2024-10-02 11:00 | 10 | 2 | 11 | 2.658% | 32.58%
2024-10-02 12:00 | 10 | 2 | 12 | 7.189% | 31.36%
2024-10-02 13:00 | 10 | 2 | 13 | 5.26% | 33.93%
2024-10-02 14:00 | 10 | 2 | 14 | 2.363% | 34.33%
2024-10-02 15:00 | 10 | 2 | 15 | 8.882% | 34.24%
2024-10-02 16:00 | 10 | 2 | 16 | 3.164% | 34.35%
2024-10-02 17:00 | 10 | 2 | 17 | 0.5262% | 35.61%
2024-10-02 18:00 | 10 | 2 | 18 | 0% | 36.76%
2024-10-02 19:00 | 10 | 2 | 19 | 0% | 37.39%
2024-10-02 20:00 | 10 | 2 | 20 | 0% | 36.87%
2024-10-02 21:00 | 10 | 2 | 21 | 0% | 36.08%
2024-10-02 22:00 | 10 | 2 | 22 | 0% | 35.61%
2024-10-02 23:00 | 10 | 2 | 23 | 0% | 35.16%
2024-10-03 | 10 | 3 | 0 | 0% | 43.55%
2024-10-03 01:00 | 10 | 3 | 1 | 0% | 34.09%
2024-10-03 02:00 | 10 | 3 | 2 | 0% | 34.43%
2024-10-03 03:00 | 10 | 3 | 3 | 0% | 34.6%
2024-10-03 04:00 | 10 | 3 | 4 | 0% | 34.81%
2024-10-03 05:00 | 10 | 3 | 5 | 0% | 34.53%
2024-10-03 06:00 | 10 | 3 | 6 | 0% | 33.97%
2024-10-03 07:00 | 10 | 3 | 7 | 4.886% | 32.89%
2024-10-03 08:00 | 10 | 3 | 8 | 9.596% | 30.92%
2024-10-03 09:00 | 10 | 3 | 9 | 13.09% | 29.4%
2024-10-03 10:00 | 10 | 3 | 10 | 12.31% | 29.3%
2024-10-03 11:00 | 10 | 3 | 11 | 19.49% | 30.23%
2024-10-03 12:00 | 10 | 3 | 12 | 12.31% | 31.34%
2024-10-03 13:00 | 10 | 3 | 13 | 19.46% | 32.01%
2024-10-03 14:00 | 10 | 3 | 14 | 12.2% | 32.58%
2024-10-03 15:00 | 10 | 3 | 15 | 7.062% | 32.47%
2024-10-03 16:00 | 10 | 3 | 16 | 4.499% | 33.14%
2024-10-03 17:00 | 10 | 3 | 17 | 0.1893% | 35.63%
2024-10-03 18:00 | 10 | 3 | 18 | 0% | 38.55%
2024-10-03 19:00 | 10 | 3 | 19 | 0% | 41.66%
2024-10-03 20:00 | 10 | 3 | 20 | 0% | 43.77%
2024-10-03 21:00 | 10 | 3 | 21 | 0% | 44.67%
2024-10-03 22:00 | 10 | 3 | 22 | 0% | 44.55%
2024-10-03 23:00 | 10 | 3 | 23 | 0% | 44.92%
2024-10-04 | 10 | 4 | 0 | 0% | 35.93%
2024-10-04 01:00 | 10 | 4 | 1 | 0% | 44.09%
2024-10-04 02:00 | 10 | 4 | 2 | 0% | 43.28%
2024-10-04 03:00 | 10 | 4 | 3 | 0% | 42.81%
2024-10-04 04:00 | 10 | 4 | 4 | 0% | 42.92%
2024-10-04 05:00 | 10 | 4 | 5 | 0% | 43.54%
2024-10-04 06:00 | 10 | 4 | 6 | 0% | 43.68%
2024-10-04 07:00 | 10 | 4 | 7 | 0.8217% | 42.1%
2024-10-04 08:00 | 10 | 4 | 8 | 2.892% | 40.36%
2024-10-04 09:00 | 10 | 4 | 9 | 4.524% | 39.2%
2024-10-04 10:00 | 10 | 4 | 10 | 8.231% | 38.71%
2024-10-04 11:00 | 10 | 4 | 11 | 10.73% | 38.87%
2024-10-04 12:00 | 10 | 4 | 12 | 6.681% | 38.84%
2024-10-04 13:00 | 10 | 4 | 13 | 5.314% | 39%
2024-10-04 14:00 | 10 | 4 | 14 | 4.713% | 38.92%
2024-10-04 15:00 | 10 | 4 | 15 | 11.06% | 38.63%
2024-10-04 16:00 | 10 | 4 | 16 | 6.048% | 38.14%
2024-10-04 17:00 | 10 | 4 | 17 | 0.3888% | 38.2%
2024-10-04 18:00 | 10 | 4 | 18 | 0% | 39.09%
2024-10-04 19:00 | 10 | 4 | 19 | 0% | 38.69%
2024-10-04 20:00 | 10 | 4 | 20 | 0% | 38.58%
2024-10-04 21:00 | 10 | 4 | 21 | 0% | 37.94%
2024-10-04 22:00 | 10 | 4 | 22 | 0% | 36.62%
2024-10-04 23:00 | 10 | 4 | 23 | 0% | 36.27%
2024-10-05 | 10 | 5 | 0 | 0% | 36.35%
2024-10-05 01:00 | 10 | 5 | 1 | 0% | 35.75%
2024-10-05 02:00 | 10 | 5 | 2 | 0% | 35.78%
2024-10-05 03:00 | 10 | 5 | 3 | 0% | 35.88%
2024-10-05 04:00 | 10 | 5 | 4 | 0% | 36.15%
2024-10-05 05:00 | 10 | 5 | 5 | 0% | 36.47%
2024-10-05 06:00 | 10 | 5 | 6 | 0.6334% | 35.87%
2024-10-05 07:00 | 10 | 5 | 7 | 7.278% | 33.07%
2024-10-05 08:00 | 10 | 5 | 8 | 25.96% | 30.26%
2024-10-05 09:00 | 10 | 5 | 9 | 42.19% | 28.25%
2024-10-05 10:00 | 10 | 5 | 10 | 49.54% | 26.58%
2024-10-05 11:00 | 10 | 5 | 11 | 58.09% | 25.36%
2024-10-05 12:00 | 10 | 5 | 12 | 57.05% | 24.37%
2024-10-05 13:00 | 10 | 5 | 13 | 51.28% | 24.07%
2024-10-05 14:00 | 10 | 5 | 14 | 41.05% | 24.56%
2024-10-05 15:00 | 10 | 5 | 15 | 21.71% | 25.03%
2024-10-05 16:00 | 10 | 5 | 16 | 6.455% | 26.07%
2024-10-05 17:00 | 10 | 5 | 17 | 0% | 28.82%
2024-10-05 18:00 | 10 | 5 | 18 | 0% | 31.77%
2024-10-05 19:00 | 10 | 5 | 19 | 0% | 33.88%
2024-10-05 20:00 | 10 | 5 | 20 | 0% | 34.63%
2024-10-05 21:00 | 10 | 5 | 21 | 0% | 34.95%
2024-10-05 22:00 | 10 | 5 | 22 | 0% | 34.87%
2024-10-05 23:00 | 10 | 5 | 23 | 0% | 35.56%
2024-10-06 | 10 | 6 | 0 | 0% | 37.82%
2024-10-06 01:00 | 10 | 6 | 1 | 0% | 37.06%
2024-10-06 02:00 | 10 | 6 | 2 | 0% | 37.38%
2024-10-06 03:00 | 10 | 6 | 3 | 0% | 39.99%
2024-10-06 04:00 | 10 | 6 | 4 | 0% | 37.36%
2024-10-06 05:00 | 10 | 6 | 5 | 0% | 37.39%
2024-10-06 06:00 | 10 | 6 | 6 | 0.4764% | 37.16%
2024-10-06 07:00 | 10 | 6 | 7 | 12.73% | 35.91%
2024-10-06 08:00 | 10 | 6 | 8 | 31.16% | 34.37%
2024-10-06 09:00 | 10 | 6 | 9 | 47.07% | 33.56%
2024-10-06 10:00 | 10 | 6 | 10 | 58.34% | 34%
2024-10-06 11:00 | 10 | 6 | 11 | 64.28% | 34.13%
2024-10-06 12:00 | 10 | 6 | 12 | 63.92% | 34.38%
2024-10-06 13:00 | 10 | 6 | 13 | 57.3% | 34.95%
2024-10-06 14:00 | 10 | 6 | 14 | 45.87% | 38.07%
2024-10-06 15:00 | 10 | 6 | 15 | 29.24% | 34.54%
2024-10-06 16:00 | 10 | 6 | 16 | 10.17% | 37.62%
2024-10-06 17:00 | 10 | 6 | 17 | 0% | 35.59%
2024-10-06 18:00 | 10 | 6 | 18 | 0% | 36.42%
2024-10-06 19:00 | 10 | 6 | 19 | 0% | 37.56%
2024-10-06 20:00 | 10 | 6 | 20 | 0% | 38.23%
2024-10-06 21:00 | 10 | 6 | 21 | 0% | 38.76%
2024-10-06 22:00 | 10 | 6 | 22 | 0% | 38.23%
2024-10-06 23:00 | 10 | 6 | 23 | 0% | 38.18%
2024-10-07 | 10 | 7 | 0 | 0% | 38.96%
2024-10-07 01:00 | 10 | 7 | 1 | 0% | 37.62%
2024-10-07 02:00 | 10 | 7 | 2 | 0% | 37.46%
2024-10-07 03:00 | 10 | 7 | 3 | 0% | 37.41%
2024-10-07 04:00 | 10 | 7 | 4 | 0% | 37.69%
2024-10-07 05:00 | 10 | 7 | 5 | 0% | 37.9%
2024-10-07 06:00 | 10 | 7 | 6 | 0% | 38.69%
2024-10-07 07:00 | 10 | 7 | 7 | 1.368% | 37.57%
2024-10-07 08:00 | 10 | 7 | 8 | 4.248% | 35.81%
2024-10-07 09:00 | 10 | 7 | 9 | 5.933% | 35.34%
2024-10-07 10:00 | 10 | 7 | 10 | 7.304% | 35%
2024-10-07 11:00 | 10 | 7 | 11 | 9.614% | 34.8%
2024-10-07 12:00 | 10 | 7 | 12 | 11.45% | 34.67%
2024-10-07 13:00 | 10 | 7 | 13 | 7.142% | 34.67%
2024-10-07 14:00 | 10 | 7 | 14 | 6.254% | 34.3%
2024-10-07 15:00 | 10 | 7 | 15 | 3.801% | 34.39%
2024-10-07 16:00 | 10 | 7 | 16 | 2.687% | 34.54%
2024-10-07 17:00 | 10 | 7 | 17 | 0% | 42.18%
2024-10-07 18:00 | 10 | 7 | 18 | 0% | 36.81%
2024-10-07 19:00 | 10 | 7 | 19 | 0% | 37.45%
2024-10-07 20:00 | 10 | 7 | 20 | 0% | 38.61%
2024-10-07 21:00 | 10 | 7 | 21 | 0% | 40.41%
2024-10-07 22:00 | 10 | 7 | 22 | 0% | 39.2%
2024-10-07 23:00 | 10 | 7 | 23 | 0% | 39.46%
2024-10-08 | 10 | 8 | 0 | 0% | 32.61%
2024-10-08 01:00 | 10 | 8 | 1 | 0% | 38.93%
2024-10-08 02:00 | 10 | 8 | 2 | 0% | 38.82%
2024-10-08 03:00 | 10 | 8 | 3 | 0% | 39.28%
2024-10-08 04:00 | 10 | 8 | 4 | 0% | 39.89%
2024-10-08 05:00 | 10 | 8 | 5 | 0% | 40.07%
2024-10-08 06:00 | 10 | 8 | 6 | 0% | 40.03%
2024-10-08 07:00 | 10 | 8 | 7 | 12.25% | 39.54%
2024-10-08 08:00 | 10 | 8 | 8 | 31.26% | 38.69%
2024-10-08 09:00 | 10 | 8 | 9 | 46.89% | 38.45%
2024-10-08 10:00 | 10 | 8 | 10 | 57.49% | 38.19%
2024-10-08 11:00 | 10 | 8 | 11 | 62.69% | 38.5%
2024-10-08 12:00 | 10 | 8 | 12 | 44.74% | 38.23%
2024-10-08 13:00 | 10 | 8 | 13 | 34.93% | 37.56%
2024-10-08 14:00 | 10 | 8 | 14 | 30.14% | 36.63%
2024-10-08 15:00 | 10 | 8 | 15 | 12.77% | 35.4%
2024-10-08 16:00 | 10 | 8 | 16 | 3.914% | 34.8%
2024-10-08 17:00 | 10 | 8 | 17 | 0% | 35.87%
2024-10-08 18:00 | 10 | 8 | 18 | 0% | 37.14%
2024-10-08 19:00 | 10 | 8 | 19 | 0% | 37.56%
2024-10-08 20:00 | 10 | 8 | 20 | 0% | 36.76%
2024-10-08 21:00 | 10 | 8 | 21 | 0% | 36.07%
2024-10-08 22:00 | 10 | 8 | 22 | 0% | 34.69%
2024-10-08 23:00 | 10 | 8 | 23 | 0% | 33.63%
2024-10-09 | 10 | 9 | 0 | 0% | 36.85%
2024-10-09 01:00 | 10 | 9 | 1 | 0% | 31.95%
2024-10-09 02:00 | 10 | 9 | 2 | 0% | 31.57%
2024-10-09 03:00 | 10 | 9 | 3 | 0% | 31.55%
2024-10-09 04:00 | 10 | 9 | 4 | 0% | 33.25%
2024-10-09 05:00 | 10 | 9 | 5 | 0% | 33.11%
2024-10-09 06:00 | 10 | 9 | 6 | 0% | 33.86%
2024-10-09 07:00 | 10 | 9 | 7 | 11.68% | 34.18%
2024-10-09 08:00 | 10 | 9 | 8 | 30.52% | 34.04%
2024-10-09 09:00 | 10 | 9 | 9 | 45.92% | 33.93%
2024-10-09 10:00 | 10 | 9 | 10 | 56.42% | 34.37%
2024-10-09 11:00 | 10 | 9 | 11 | 55.63% | 35.56%
2024-10-09 12:00 | 10 | 9 | 12 | 41.04% | 36.51%
2024-10-09 13:00 | 10 | 9 | 13 | 44.61% | 36.83%
2024-10-09 14:00 | 10 | 9 | 14 | 37.63% | 36.39%
2024-10-09 15:00 | 10 | 9 | 15 | 27.02% | 36.24%
2024-10-09 16:00 | 10 | 9 | 16 | 8.167% | 36.47%
2024-10-09 17:00 | 10 | 9 | 17 | 0% | 37.43%
2024-10-09 18:00 | 10 | 9 | 18 | 0% | 38.96%
2024-10-09 19:00 | 10 | 9 | 19 | 0% | 40.12%
2024-10-09 20:00 | 10 | 9 | 20 | 0% | 40.27%
2024-10-09 21:00 | 10 | 9 | 21 | 0% | 37.18%
2024-10-09 22:00 | 10 | 9 | 22 | 0% | 39%
2024-10-09 23:00 | 10 | 9 | 23 | 0% | 38.2%
2024-10-10 | 10 | 10 | 0 | 0% | 44.46%
2024-10-10 01:00 | 10 | 10 | 1 | 0% | 35.82%
2024-10-10 02:00 | 10 | 10 | 2 | 0% | 34.76%
2024-10-10 03:00 | 10 | 10 | 3 | 0% | 34.15%
2024-10-10 04:00 | 10 | 10 | 4 | 0% | 33.51%
2024-10-10 05:00 | 10 | 10 | 5 | 0% | 33.14%
2024-10-10 06:00 | 10 | 10 | 6 | 0% | 32.38%
2024-10-10 07:00 | 10 | 10 | 7 | 9.29% | 31.27%
2024-10-10 08:00 | 10 | 10 | 8 | 29.21% | 29.81%
2024-10-10 09:00 | 10 | 10 | 9 | 44.87% | 28.47%
2024-10-10 10:00 | 10 | 10 | 10 | 48.74% | 27.87%
2024-10-10 11:00 | 10 | 10 | 11 | 44% | 28.23%
2024-10-10 12:00 | 10 | 10 | 12 | 29.73% | 29.63%
2024-10-10 13:00 | 10 | 10 | 13 | 16.27% | 31.2%
2024-10-10 14:00 | 10 | 10 | 14 | 10.03% | 32.44%
2024-10-10 15:00 | 10 | 10 | 15 | 3.803% | 33.65%
2024-10-10 16:00 | 10 | 10 | 16 | 1.489% | 35.48%
2024-10-10 17:00 | 10 | 10 | 17 | 0% | 38.38%
2024-10-10 18:00 | 10 | 10 | 18 | 0% | 40.88%
2024-10-10 19:00 | 10 | 10 | 19 | 0% | 42.81%
2024-10-10 20:00 | 10 | 10 | 20 | 0% | 47.48%
2024-10-10 21:00 | 10 | 10 | 21 | 0% | 43.85%
2024-10-10 22:00 | 10 | 10 | 22 | 0% | 43.46%
2024-10-10 23:00 | 10 | 10 | 23 | 0% | 42.91%
2024-10-11 | 10 | 11 | 0 | 0% | 40.88%
2024-10-11 01:00 | 10 | 11 | 1 | 0% | 41.56%
2024-10-11 02:00 | 10 | 11 | 2 | 0% | 41.25%
2024-10-11 03:00 | 10 | 11 | 3 | 0% | 40.65%
2024-10-11 04:00 | 10 | 11 | 4 | 0% | 40.21%
2024-10-11 05:00 | 10 | 11 | 5 | 0% | 39.5%
2024-10-11 06:00 | 10 | 11 | 6 | 0% | 39.09%
2024-10-11 07:00 | 10 | 11 | 7 | 2.853% | 37.21%
2024-10-11 08:00 | 10 | 11 | 8 | 11.78% | 35.02%
2024-10-11 09:00 | 10 | 11 | 9 | 13.93% | 33.02%
2024-10-11 10:00 | 10 | 11 | 10 | 25.92% | 31.82%
2024-10-11 11:00 | 10 | 11 | 11 | 7.82% | 31.58%
2024-10-11 12:00 | 10 | 11 | 12 | 9.089% | 32.09%
2024-10-11 13:00 | 10 | 11 | 13 | 6.508% | 32.42%
2024-10-11 14:00 | 10 | 11 | 14 | 5.255% | 36.18%
2024-10-11 15:00 | 10 | 11 | 15 | 2.208% | 36.7%
2024-10-11 16:00 | 10 | 11 | 16 | 0.7218% | 34.2%
2024-10-11 17:00 | 10 | 11 | 17 | 0% | 35.71%
2024-10-11 18:00 | 10 | 11 | 18 | 0% | 37.64%
2024-10-11 19:00 | 10 | 11 | 19 | 0% | 39.27%
2024-10-11 20:00 | 10 | 11 | 20 | 0% | 40.04%
2024-10-11 21:00 | 10 | 11 | 21 | 0% | 40.27%
2024-10-11 22:00 | 10 | 11 | 22 | 0% | 40.55%
2024-10-11 23:00 | 10 | 11 | 23 | 0% | 40.83%
2024-10-12 | 10 | 12 | 0 | 0% | 37.87%
2024-10-12 01:00 | 10 | 12 | 1 | 0% | 39.89%
2024-10-12 02:00 | 10 | 12 | 2 | 0% | 39.53%
2024-10-12 03:00 | 10 | 12 | 3 | 0% | 38.97%
2024-10-12 04:00 | 10 | 12 | 4 | 0% | 38.17%
2024-10-12 05:00 | 10 | 12 | 5 | 0% | 37.29%
2024-10-12 06:00 | 10 | 12 | 6 | 0% | 36.48%
2024-10-12 07:00 | 10 | 12 | 7 | 1.873% | 35.17%
2024-10-12 08:00 | 10 | 12 | 8 | 4.951% | 33.38%
2024-10-12 09:00 | 10 | 12 | 9 | 11.71% | 31.8%
2024-10-12 10:00 | 10 | 12 | 10 | 11.54% | 31.62%
2024-10-12 11:00 | 10 | 12 | 11 | 15.26% | 31.92%
2024-10-12 12:00 | 10 | 12 | 12 | 11.42% | 33.14%
2024-10-12 13:00 | 10 | 12 | 13 | 10.39% | 36.85%
2024-10-12 14:00 | 10 | 12 | 14 | 3.778% | 34.58%
2024-10-12 15:00 | 10 | 12 | 15 | 10.52% | 35.1%
2024-10-12 16:00 | 10 | 12 | 16 | 3.291% | 36.1%
2024-10-12 17:00 | 10 | 12 | 17 | 0% | 37.91%
2024-10-12 18:00 | 10 | 12 | 18 | 0% | 39.62%
2024-10-12 19:00 | 10 | 12 | 19 | 0% | 40.85%
2024-10-12 20:00 | 10 | 12 | 20 | 0% | 40.89%
2024-10-12 21:00 | 10 | 12 | 21 | 0% | 39.82%
2024-10-12 22:00 | 10 | 12 | 22 | 0% | 38.83%
2024-10-12 23:00 | 10 | 12 | 23 | 0% | 40.88%
2024-10-13 | 10 | 13 | 0 | 0% | 30.08%
2024-10-13 01:00 | 10 | 13 | 1 | 0% | 36.89%
2024-10-13 02:00 | 10 | 13 | 2 | 0% | 35.98%
2024-10-13 03:00 | 10 | 13 | 3 | 0% | 34.78%
2024-10-13 04:00 | 10 | 13 | 4 | 0% | 33.98%
2024-10-13 05:00 | 10 | 13 | 5 | 0% | 33.42%
2024-10-13 06:00 | 10 | 13 | 6 | 0% | 32.39%
2024-10-13 07:00 | 10 | 13 | 7 | 5.003% | 30.06%
2024-10-13 08:00 | 10 | 13 | 8 | 20.55% | 26.55%
2024-10-13 09:00 | 10 | 13 | 9 | 41.15% | 23.76%
2024-10-13 10:00 | 10 | 13 | 10 | 36.05% | 21.85%
2024-10-13 11:00 | 10 | 13 | 11 | 22.19% | 21.57%
2024-10-13 12:00 | 10 | 13 | 12 | 17.31% | 21.01%
2024-10-13 13:00 | 10 | 13 | 13 | 23.73% | 20.66%
2024-10-13 14:00 | 10 | 13 | 14 | 6.838% | 20.79%
2024-10-13 15:00 | 10 | 13 | 15 | 4.395% | 21.2%
2024-10-13 16:00 | 10 | 13 | 16 | 1.308% | 21.85%
2024-10-13 17:00 | 10 | 13 | 17 | 0% | 22.84%
2024-10-13 18:00 | 10 | 13 | 18 | 0% | 23.85%
2024-10-13 19:00 | 10 | 13 | 19 | 0% | 24.73%
2024-10-13 20:00 | 10 | 13 | 20 | 0% | 25.76%
2024-10-13 21:00 | 10 | 13 | 21 | 0% | 26.62%
2024-10-13 22:00 | 10 | 13 | 22 | 0% | 27.59%
2024-10-13 23:00 | 10 | 13 | 23 | 0% | 28.99%
2024-10-14 | 10 | 14 | 0 | 0% | 42.05%
2024-10-14 01:00 | 10 | 14 | 1 | 0% | 31.12%
2024-10-14 02:00 | 10 | 14 | 2 | 0% | 31.98%
2024-10-14 03:00 | 10 | 14 | 3 | 0% | 32.76%
2024-10-14 04:00 | 10 | 14 | 4 | 0% | 33.23%
2024-10-14 05:00 | 10 | 14 | 5 | 0% | 33.76%
2024-10-14 06:00 | 10 | 14 | 6 | 0% | 32.9%
2024-10-14 07:00 | 10 | 14 | 7 | 0% | 34.33%
2024-10-14 08:00 | 10 | 14 | 8 | 1.817% | 34.03%
2024-10-14 09:00 | 10 | 14 | 9 | 4.207% | 33.76%
2024-10-14 10:00 | 10 | 14 | 10 | 8.732% | 33.92%
2024-10-14 11:00 | 10 | 14 | 11 | 12.24% | 34.1%
2024-10-14 12:00 | 10 | 14 | 12 | 8.175% | 33.97%
2024-10-14 13:00 | 10 | 14 | 13 | 8.847% | 34.12%
2024-10-14 14:00 | 10 | 14 | 14 | 8.358% | 33.92%
2024-10-14 15:00 | 10 | 14 | 15 | 7.039% | 33.77%
2024-10-14 16:00 | 10 | 14 | 16 | 1.41% | 34.81%
2024-10-14 17:00 | 10 | 14 | 17 | 0% | 37.41%
2024-10-14 18:00 | 10 | 14 | 18 | 0% | 39.45%
2024-10-14 19:00 | 10 | 14 | 19 | 0% | 41.09%
2024-10-14 20:00 | 10 | 14 | 20 | 0% | 42.09%
2024-10-14 21:00 | 10 | 14 | 21 | 0% | 42.7%
2024-10-14 22:00 | 10 | 14 | 22 | 0% | 43.07%
2024-10-14 23:00 | 10 | 14 | 23 | 0% | 42.36%
2024-10-15 | 10 | 15 | 0 | 0% | 35.72%
2024-10-15 01:00 | 10 | 15 | 1 | 0% | 40.96%
2024-10-15 02:00 | 10 | 15 | 2 | 0% | 39.98%
2024-10-15 03:00 | 10 | 15 | 3 | 0% | 39.49%
2024-10-15 04:00 | 10 | 15 | 4 | 0% | 38.78%
2024-10-15 05:00 | 10 | 15 | 5 | 0% | 38.58%
2024-10-15 06:00 | 10 | 15 | 6 | 0% | 37.74%
2024-10-15 07:00 | 10 | 15 | 7 | 1.303% | 36.21%
2024-10-15 08:00 | 10 | 15 | 8 | 5.642% | 34.51%
2024-10-15 09:00 | 10 | 15 | 9 | 10.23% | 32.57%
2024-10-15 10:00 | 10 | 15 | 10 | 14.04% | 30.78%
2024-10-15 11:00 | 10 | 15 | 11 | 27.73% | 29.36%
2024-10-15 12:00 | 10 | 15 | 12 | 6.466% | 28.33%
2024-10-15 13:00 | 10 | 15 | 13 | 4.906% | 27.76%
2024-10-15 14:00 | 10 | 15 | 14 | 2.433% | 27.52%
2024-10-15 15:00 | 10 | 15 | 15 | 1.55% | 27.2%
2024-10-15 16:00 | 10 | 15 | 16 | 1.321% | 29.33%
2024-10-15 17:00 | 10 | 15 | 17 | 0% | 30.32%
2024-10-15 18:00 | 10 | 15 | 18 | 0% | 32.56%
2024-10-15 19:00 | 10 | 15 | 19 | 0% | 34.05%
2024-10-15 20:00 | 10 | 15 | 20 | 0% | 35.07%
2024-10-15 21:00 | 10 | 15 | 21 | 0% | 35.46%
2024-10-15 22:00 | 10 | 15 | 22 | 0% | 35.94%
2024-10-15 23:00 | 10 | 15 | 23 | 0% | 35.45%
2024-10-16 | 10 | 16 | 0 | 0% | 32.46%
2024-10-16 01:00 | 10 | 16 | 1 | 0% | 35.86%
2024-10-16 02:00 | 10 | 16 | 2 | 0% | 36.05%
2024-10-16 03:00 | 10 | 16 | 3 | 0% | 36.15%
2024-10-16 04:00 | 10 | 16 | 4 | 0% | 36.11%
2024-10-16 05:00 | 10 | 16 | 5 | 0% | 36.36%
2024-10-16 06:00 | 10 | 16 | 6 | 0% | 36.17%
2024-10-16 07:00 | 10 | 16 | 7 | 1.199% | 34.72%
2024-10-16 08:00 | 10 | 16 | 8 | 4.693% | 32.99%
2024-10-16 09:00 | 10 | 16 | 9 | 7.038% | 31.32%
2024-10-16 10:00 | 10 | 16 | 10 | 9.177% | 29.85%
2024-10-16 11:00 | 10 | 16 | 11 | 6.452% | 29.3%
2024-10-16 12:00 | 10 | 16 | 12 | 3.334% | 29.11%
2024-10-16 13:00 | 10 | 16 | 13 | 6.209% | 29.47%
2024-10-16 14:00 | 10 | 16 | 14 | 5.067% | 29.94%
2024-10-16 15:00 | 10 | 16 | 15 | 2.994% | 29.88%
2024-10-16 16:00 | 10 | 16 | 16 | 1.333% | 31.15%
2024-10-16 17:00 | 10 | 16 | 17 | 0% | 33.95%
2024-10-16 18:00 | 10 | 16 | 18 | 0% | 35.53%
2024-10-16 19:00 | 10 | 16 | 19 | 0% | 36.41%
2024-10-16 20:00 | 10 | 16 | 20 | 0% | 36.53%
2024-10-16 21:00 | 10 | 16 | 21 | 0% | 35.64%
2024-10-16 22:00 | 10 | 16 | 22 | 0% | 34.72%
2024-10-16 23:00 | 10 | 16 | 23 | 0% | 33.75%
2024-10-17 | 10 | 17 | 0 | 0% | 33.33%
2024-10-17 01:00 | 10 | 17 | 1 | 0% | 31.67%
2024-10-17 02:00 | 10 | 17 | 2 | 0% | 30.75%
2024-10-17 03:00 | 10 | 17 | 3 | 0% | 30.71%
2024-10-17 04:00 | 10 | 17 | 4 | 0% | 30.96%
2024-10-17 05:00 | 10 | 17 | 5 | 0% | 31.26%
2024-10-17 06:00 | 10 | 17 | 6 | 0% | 31.21%
2024-10-17 07:00 | 10 | 17 | 7 | 2.172% | 30.58%
2024-10-17 08:00 | 10 | 17 | 8 | 7.111% | 29.16%
2024-10-17 09:00 | 10 | 17 | 9 | 10.72% | 27.03%
2024-10-17 10:00 | 10 | 17 | 10 | 8.4% | 26.41%
2024-10-17 11:00 | 10 | 17 | 11 | 7.737% | 26.47%
2024-10-17 12:00 | 10 | 17 | 12 | 4.988% | 26.88%
2024-10-17 13:00 | 10 | 17 | 13 | 3.736% | 27.02%
2024-10-17 14:00 | 10 | 17 | 14 | 3.004% | 27.58%
2024-10-17 15:00 | 10 | 17 | 15 | 1.741% | 28.67%
2024-10-17 16:00 | 10 | 17 | 16 | 0.8539% | 30.54%
2024-10-17 17:00 | 10 | 17 | 17 | 0% | 32.75%
2024-10-17 18:00 | 10 | 17 | 18 | 0% | 34.64%
2024-10-17 19:00 | 10 | 17 | 19 | 0% | 36.04%
2024-10-17 20:00 | 10 | 17 | 20 | 0% | 35.66%
2024-10-17 21:00 | 10 | 17 | 21 | 0% | 33.45%
2024-10-17 22:00 | 10 | 17 | 22 | 0% | 34.64%
2024-10-17 23:00 | 10 | 17 | 23 | 0% | 34.09%
2024-10-18 | 10 | 18 | 0 | 0% | 26.85%
2024-10-18 01:00 | 10 | 18 | 1 | 0% | 32.61%
2024-10-18 02:00 | 10 | 18 | 2 | 0% | 31.5%
2024-10-18 03:00 | 10 | 18 | 3 | 0% | 30.52%
2024-10-18 04:00 | 10 | 18 | 4 | 0% | 29.47%
2024-10-18 05:00 | 10 | 18 | 5 | 0% | 28.71%
2024-10-18 06:00 | 10 | 18 | 6 | 0% | 27.75%
2024-10-18 07:00 | 10 | 18 | 7 | 0.8409% | 25.41%
2024-10-18 08:00 | 10 | 18 | 8 | 6.867% | 23.02%
2024-10-18 09:00 | 10 | 18 | 9 | 8.724% | 20.36%
2024-10-18 10:00 | 10 | 18 | 10 | 7.352% | 18.07%
2024-10-18 11:00 | 10 | 18 | 11 | 10.12% | 16.59%
2024-10-18 12:00 | 10 | 18 | 12 | 15.23% | 15.91%
2024-10-18 13:00 | 10 | 18 | 13 | 9.312% | 15.55%
2024-10-18 14:00 | 10 | 18 | 14 | 7.802% | 15.45%
2024-10-18 15:00 | 10 | 18 | 15 | 6.069% | 16.2%
2024-10-18 16:00 | 10 | 18 | 16 | 0.6815% | 18.36%
2024-10-18 17:00 | 10 | 18 | 17 | 0% | 20.93%
2024-10-18 18:00 | 10 | 18 | 18 | 0% | 23.62%
2024-10-18 19:00 | 10 | 18 | 19 | 0% | 25.08%
2024-10-18 20:00 | 10 | 18 | 20 | 0% | 27.49%
2024-10-18 21:00 | 10 | 18 | 21 | 0% | 25.71%
2024-10-18 22:00 | 10 | 18 | 22 | 0% | 25.91%
2024-10-18 23:00 | 10 | 18 | 23 | 0% | 26.46%
2024-10-19 | 10 | 19 | 0 | 0% | 31.54%
2024-10-19 01:00 | 10 | 19 | 1 | 0% | 27.28%
2024-10-19 02:00 | 10 | 19 | 2 | 0% | 27.97%
2024-10-19 03:00 | 10 | 19 | 3 | 0% | 28.34%
2024-10-19 04:00 | 10 | 19 | 4 | 0% | 28.78%
2024-10-19 05:00 | 10 | 19 | 5 | 0% | 28.87%
2024-10-19 06:00 | 10 | 19 | 6 | 0% | 28.91%
2024-10-19 07:00 | 10 | 19 | 7 | 1.708% | 27.94%
2024-10-19 08:00 | 10 | 19 | 8 | 4.869% | 26.23%
2024-10-19 09:00 | 10 | 19 | 9 | 10.88% | 24.73%
2024-10-19 10:00 | 10 | 19 | 10 | 13.04% | 23.56%
2024-10-19 11:00 | 10 | 19 | 11 | 12.9% | 22.49%
2024-10-19 12:00 | 10 | 19 | 12 | 8.233% | 21.64%
2024-10-19 13:00 | 10 | 19 | 13 | 5.725% | 21.58%
2024-10-19 14:00 | 10 | 19 | 14 | 3.52% | 21.6%
2024-10-19 15:00 | 10 | 19 | 15 | 2.651% | 21.87%
2024-10-19 16:00 | 10 | 19 | 16 | 0.3213% | 23.79%
2024-10-19 17:00 | 10 | 19 | 17 | 0% | 25.54%
2024-10-19 18:00 | 10 | 19 | 18 | 0% | 27.18%
2024-10-19 19:00 | 10 | 19 | 19 | 0% | 28.72%
2024-10-19 20:00 | 10 | 19 | 20 | 0% | 29.73%
2024-10-19 21:00 | 10 | 19 | 21 | 0% | 30.23%
2024-10-19 22:00 | 10 | 19 | 22 | 0% | 30.72%
2024-10-19 23:00 | 10 | 19 | 23 | 0% | 31.29%
2024-10-20 | 10 | 20 | 0 | 0% | 45.31%
2024-10-20 01:00 | 10 | 20 | 1 | 0% | 35.18%
2024-10-20 02:00 | 10 | 20 | 2 | 0% | 33.64%
2024-10-20 03:00 | 10 | 20 | 3 | 0% | 35.02%
2024-10-20 04:00 | 10 | 20 | 4 | 0% | 39.41%
2024-10-20 05:00 | 10 | 20 | 5 | 0% | 37.31%
2024-10-20 06:00 | 10 | 20 | 6 | 0% | 38.09%
2024-10-20 07:00 | 10 | 20 | 7 | 0% | 41.29%
2024-10-20 08:00 | 10 | 20 | 8 | 2.643% | 37.62%
2024-10-20 09:00 | 10 | 20 | 9 | 6.891% | 37.04%
2024-10-20 10:00 | 10 | 20 | 10 | 7.711% | 36.39%
2024-10-20 11:00 | 10 | 20 | 11 | 6.546% | 35.97%
2024-10-20 12:00 | 10 | 20 | 12 | 5.117% | 35.39%
2024-10-20 13:00 | 10 | 20 | 13 | 2.624% | 35.42%
2024-10-20 14:00 | 10 | 20 | 14 | 1.902% | 33.28%
2024-10-20 15:00 | 10 | 20 | 15 | 1.291% | 34.15%
2024-10-20 16:00 | 10 | 20 | 16 | 0% | 36.13%
2024-10-20 17:00 | 10 | 20 | 17 | 0% | 38.6%
2024-10-20 18:00 | 10 | 20 | 18 | 0% | 41.02%
2024-10-20 19:00 | 10 | 20 | 19 | 0% | 42.71%
2024-10-20 20:00 | 10 | 20 | 20 | 0% | 46.01%
2024-10-20 21:00 | 10 | 20 | 21 | 0% | 45.81%
2024-10-20 22:00 | 10 | 20 | 22 | 0% | 45.67%
2024-10-20 23:00 | 10 | 20 | 23 | 0% | 45.35%
2024-10-21 | 10 | 21 | 0 | 0% | 48.93%
2024-10-21 01:00 | 10 | 21 | 1 | 0% | 45.57%
2024-10-21 02:00 | 10 | 21 | 2 | 0% | 45.57%
2024-10-21 03:00 | 10 | 21 | 3 | 0% | 46.35%
2024-10-21 04:00 | 10 | 21 | 4 | 0% | 46.81%
2024-10-21 05:00 | 10 | 21 | 5 | 0% | 47.73%
2024-10-21 06:00 | 10 | 21 | 6 | 0% | 47.41%
2024-10-21 07:00 | 10 | 21 | 7 | 0% | 46.65%
2024-10-21 08:00 | 10 | 21 | 8 | 1.574% | 45.66%
2024-10-21 09:00 | 10 | 21 | 9 | 3.338% | 44.92%
2024-10-21 10:00 | 10 | 21 | 10 | 5.567% | 44.64%
2024-10-21 11:00 | 10 | 21 | 11 | 4.413% | 45.04%
2024-10-21 12:00 | 10 | 21 | 12 | 4.048% | 45.57%
2024-10-21 13:00 | 10 | 21 | 13 | 3.787% | 46.22%
2024-10-21 14:00 | 10 | 21 | 14 | 2.567% | 46.74%
2024-10-21 15:00 | 10 | 21 | 15 | 1.028% | 48.19%
2024-10-21 16:00 | 10 | 21 | 16 | 0% | 49.84%
2024-10-21 17:00 | 10 | 21 | 17 | 0% | 51.52%
2024-10-21 18:00 | 10 | 21 | 18 | 0% | 52.64%
2024-10-21 19:00 | 10 | 21 | 19 | 0% | 52.74%
2024-10-21 20:00 | 10 | 21 | 20 | 0% | 52.73%
2024-10-21 21:00 | 10 | 21 | 21 | 0% | 51.91%
2024-10-21 22:00 | 10 | 21 | 22 | 0% | 51.02%
2024-10-21 23:00 | 10 | 21 | 23 | 0% | 49.88%
2024-10-22 | 10 | 22 | 0 | 0% | 48.93%
2024-10-22 01:00 | 10 | 22 | 1 | 0% | 48.01%
2024-10-22 02:00 | 10 | 22 | 2 | 0% | 47.25%
2024-10-22 03:00 | 10 | 22 | 3 | 0% | 46.54%
2024-10-22 04:00 | 10 | 22 | 4 | 0% | 46.41%
2024-10-22 05:00 | 10 | 22 | 5 | 0% | 46.53%
2024-10-22 06:00 | 10 | 22 | 6 | 0% | 46.76%
2024-10-22 07:00 | 10 | 22 | 7 | 0% | 46.44%
2024-10-22 08:00 | 10 | 22 | 8 | 3.516% | 45.47%
2024-10-22 09:00 | 10 | 22 | 9 | 3.24% | 44.99%
2024-10-22 10:00 | 10 | 22 | 10 | 5.474% | 45.49%
2024-10-22 11:00 | 10 | 22 | 11 | 4.967% | 45.46%
2024-10-22 12:00 | 10 | 22 | 12 | 5.44% | 45.57%
2024-10-22 13:00 | 10 | 22 | 13 | 1.726% | 45.51%
2024-10-22 14:00 | 10 | 22 | 14 | 2.095% | 45.8%
2024-10-22 15:00 | 10 | 22 | 15 | 1.301% | 46.44%
2024-10-22 16:00 | 10 | 22 | 16 | 0% | 47.49%
2024-10-22 17:00 | 10 | 22 | 17 | 0% | 48.65%
2024-10-22 18:00 | 10 | 22 | 18 | 0% | 49.79%
2024-10-22 19:00 | 10 | 22 | 19 | 0% | 50.39%
2024-10-22 20:00 | 10 | 22 | 20 | 0% | 50.91%
2024-10-22 21:00 | 10 | 22 | 21 | 0% | 50.67%
2024-10-22 22:00 | 10 | 22 | 22 | 0% | 50.05%
2024-10-22 23:00 | 10 | 22 | 23 | 0% | 49.89%
2024-10-23 | 10 | 23 | 0 | 0% | 37.22%
2024-10-23 01:00 | 10 | 23 | 1 | 0% | 47.98%
2024-10-23 02:00 | 10 | 23 | 2 | 0% | 46.75%
2024-10-23 03:00 | 10 | 23 | 3 | 0% | 45.48%
2024-10-23 04:00 | 10 | 23 | 4 | 0% | 44.47%
2024-10-23 05:00 | 10 | 23 | 5 | 0% | 43.12%
2024-10-23 06:00 | 10 | 23 | 6 | 0% | 41.12%
2024-10-23 07:00 | 10 | 23 | 7 | 0.5048% | 38.62%
2024-10-23 08:00 | 10 | 23 | 8 | 3.686% | 36.17%
2024-10-23 09:00 | 10 | 23 | 9 | 7.268% | 34.29%
2024-10-23 10:00 | 10 | 23 | 10 | 5.828% | 33.47%
2024-10-23 11:00 | 10 | 23 | 11 | 7.474% | 32.23%
2024-10-23 12:00 | 10 | 23 | 12 | 6.175% | 32.16%
2024-10-23 13:00 | 10 | 23 | 13 | 6.439% | 31.7%
2024-10-23 14:00 | 10 | 23 | 14 | 2.889% | 31.18%
2024-10-23 15:00 | 10 | 23 | 15 | 1.608% | 31.29%
2024-10-23 16:00 | 10 | 23 | 16 | 0.6217% | 31.84%
2024-10-23 17:00 | 10 | 23 | 17 | 0% | 32.82%
2024-10-23 18:00 | 10 | 23 | 18 | 0% | 33.79%
2024-10-23 19:00 | 10 | 23 | 19 | 0% | 34.34%
2024-10-23 20:00 | 10 | 23 | 20 | 0% | 34.82%
2024-10-23 21:00 | 10 | 23 | 21 | 0% | 34.92%
2024-10-23 22:00 | 10 | 23 | 22 | 0% | 35.91%
2024-10-23 23:00 | 10 | 23 | 23 | 0% | 36.65%
2024-10-24 | 10 | 24 | 0 | 0% | 43.52%
2024-10-24 01:00 | 10 | 24 | 1 | 0% | 37.76%
2024-10-24 02:00 | 10 | 24 | 2 | 0% | 38.45%
2024-10-24 03:00 | 10 | 24 | 3 | 0% | 39.08%
2024-10-24 04:00 | 10 | 24 | 4 | 0% | 39.93%
2024-10-24 05:00 | 10 | 24 | 5 | 0% | 40.72%
2024-10-24 06:00 | 10 | 24 | 6 | 0% | 41.03%
2024-10-24 07:00 | 10 | 24 | 7 | 0% | 40.74%
2024-10-24 08:00 | 10 | 24 | 8 | 2.41% | 40.1%
2024-10-24 09:00 | 10 | 24 | 9 | 4.987% | 39.44%
2024-10-24 10:00 | 10 | 24 | 10 | 5.064% | 38.97%
2024-10-24 11:00 | 10 | 24 | 11 | 9.802% | 38.28%
2024-10-24 12:00 | 10 | 24 | 12 | 8.111% | 37.85%
2024-10-24 13:00 | 10 | 24 | 13 | 4.962% | 37.9%
2024-10-24 14:00 | 10 | 24 | 14 | 2.989% | 37.59%
2024-10-24 15:00 | 10 | 24 | 15 | 1.316% | 38.03%
2024-10-24 16:00 | 10 | 24 | 16 | 0% | 39.17%
2024-10-24 17:00 | 10 | 24 | 17 | 0% | 40.83%
2024-10-24 18:00 | 10 | 24 | 18 | 0% | 42.57%
2024-10-24 19:00 | 10 | 24 | 19 | 0% | 43.5%
2024-10-24 20:00 | 10 | 24 | 20 | 0% | 43.82%
2024-10-24 21:00 | 10 | 24 | 21 | 0% | 43.76%
2024-10-24 22:00 | 10 | 24 | 22 | 0% | 43.49%
2024-10-24 23:00 | 10 | 24 | 23 | 0% | 43.76%
2024-10-25 | 10 | 25 | 0 | 0% | 29.19%
2024-10-25 01:00 | 10 | 25 | 1 | 0% | 43.34%
2024-10-25 02:00 | 10 | 25 | 2 | 0% | 43.16%
2024-10-25 03:00 | 10 | 25 | 3 | 0% | 43.05%
2024-10-25 04:00 | 10 | 25 | 4 | 0% | 43.32%
2024-10-25 05:00 | 10 | 25 | 5 | 0% | 43.32%
2024-10-25 06:00 | 10 | 25 | 6 | 0% | 43.65%
2024-10-25 07:00 | 10 | 25 | 7 | 0% | 43.29%
2024-10-25 08:00 | 10 | 25 | 8 | 2.461% | 42.74%
2024-10-25 09:00 | 10 | 25 | 9 | 0.9163% | 41.67%
2024-10-25 10:00 | 10 | 25 | 10 | 2.338% | 40.99%
2024-10-25 11:00 | 10 | 25 | 11 | 4.025% | 40.52%
2024-10-25 12:00 | 10 | 25 | 12 | 2.343% | 40.64%
2024-10-25 13:00 | 10 | 25 | 13 | 13.47% | 38.34%
2024-10-25 14:00 | 10 | 25 | 14 | 18.63% | 37.41%
2024-10-25 15:00 | 10 | 25 | 15 | 9.987% | 37.04%
2024-10-25 16:00 | 10 | 25 | 16 | 0.8146% | 37.43%
2024-10-25 17:00 | 10 | 25 | 17 | 0% | 37.66%
2024-10-25 18:00 | 10 | 25 | 18 | 0% | 37.37%
2024-10-25 19:00 | 10 | 25 | 19 | 0% | 36.87%
2024-10-25 20:00 | 10 | 25 | 20 | 0% | 35.56%
2024-10-25 21:00 | 10 | 25 | 21 | 0% | 34.17%
2024-10-25 22:00 | 10 | 25 | 22 | 0% | 32.16%
2024-10-25 23:00 | 10 | 25 | 23 | 0% | 30.93%
2024-10-26 | 10 | 26 | 0 | 0% | 28.71%
2024-10-26 01:00 | 10 | 26 | 1 | 0% | 27.82%
2024-10-26 02:00 | 10 | 26 | 2 | 0% | 26.89%
2024-10-26 03:00 | 10 | 26 | 3 | 0% | 26.7%
2024-10-26 04:00 | 10 | 26 | 4 | 0% | 26.24%
2024-10-26 05:00 | 10 | 26 | 5 | 0% | 26.11%
2024-10-26 06:00 | 10 | 26 | 6 | 0% | 25.6%
2024-10-26 07:00 | 10 | 26 | 7 | 0% | 24.42%
2024-10-26 08:00 | 10 | 26 | 8 | 4.342% | 23.37%
2024-10-26 09:00 | 10 | 26 | 9 | 22.08% | 22%
2024-10-26 10:00 | 10 | 26 | 10 | 35.45% | 20.96%
2024-10-26 11:00 | 10 | 26 | 11 | 31.13% | 20.31%
2024-10-26 12:00 | 10 | 26 | 12 | 33.17% | 19.68%
2024-10-26 13:00 | 10 | 26 | 13 | 14.39% | 19.6%
2024-10-26 14:00 | 10 | 26 | 14 | 16.98% | 19.35%
2024-10-26 15:00 | 10 | 26 | 15 | 6.204% | 19.95%
2024-10-26 16:00 | 10 | 26 | 16 | 0.5519% | 21.82%
2024-10-26 17:00 | 10 | 26 | 17 | 0% | 23.47%
2024-10-26 18:00 | 10 | 26 | 18 | 0% | 25.22%
2024-10-26 19:00 | 10 | 26 | 19 | 0% | 26.27%
2024-10-26 20:00 | 10 | 26 | 20 | 0% | 27.06%
2024-10-26 21:00 | 10 | 26 | 21 | 0% | 27.68%
2024-10-26 22:00 | 10 | 26 | 22 | 0% | 27.68%
2024-10-26 23:00 | 10 | 26 | 23 | 0% | 27.9%
2024-10-27 | 10 | 27 | 0 | 0% | 40.94%
2024-10-27 01:00 | 10 | 27 | 1 | 0% | 29.19%
2024-10-27 02:00 | 10 | 27 | 2 | 0% | 30.1%
2024-10-27 03:00 | 10 | 27 | 3 | 0% | 30.98%
2024-10-27 04:00 | 10 | 27 | 4 | 0% | 32.42%
2024-10-27 05:00 | 10 | 27 | 5 | 0% | 34.11%
2024-10-27 06:00 | 10 | 27 | 6 | 0% | 35.64%
2024-10-27 07:00 | 10 | 27 | 7 | 1.121% | 36.46%
2024-10-27 08:00 | 10 | 27 | 8 | 4.278% | 36.71%
2024-10-27 09:00 | 10 | 27 | 9 | 13.64% | 36.8%
2024-10-27 10:00 | 10 | 27 | 10 | 37.02% | 36.81%
2024-10-27 11:00 | 10 | 27 | 11 | 43.12% | 36.12%
2024-10-27 12:00 | 10 | 27 | 12 | 29.82% | 35.92%
2024-10-27 13:00 | 10 | 27 | 13 | 10.68% | 35.86%
2024-10-27 14:00 | 10 | 27 | 14 | 11.21% | 35.68%
2024-10-27 15:00 | 10 | 27 | 15 | 5.454% | 36.54%
2024-10-27 16:00 | 10 | 27 | 16 | 0% | 37.85%
2024-10-27 17:00 | 10 | 27 | 17 | 0% | 39.14%
2024-10-27 18:00 | 10 | 27 | 18 | 0% | 40.34%
2024-10-27 19:00 | 10 | 27 | 19 | 0% | 41.06%
2024-10-27 20:00 | 10 | 27 | 20 | 0% | 41.18%
2024-10-27 21:00 | 10 | 27 | 21 | 0% | 41.15%
2024-10-27 22:00 | 10 | 27 | 22 | 0% | 40.86%
2024-10-27 23:00 | 10 | 27 | 23 | 0% | 40.69%
2024-10-28 | 10 | 28 | 0 | 0% | 34.06%
2024-10-28 01:00 | 10 | 28 | 1 | 0% | 41.07%
2024-10-28 02:00 | 10 | 28 | 2 | 0% | 40.38%
2024-10-28 03:00 | 10 | 28 | 3 | 0% | 40.49%
2024-10-28 04:00 | 10 | 28 | 4 | 0% | 40.45%
2024-10-28 05:00 | 10 | 28 | 5 | 0% | 40.33%
2024-10-28 06:00 | 10 | 28 | 6 | 0% | 40.22%
2024-10-28 07:00 | 10 | 28 | 7 | 0% | 39.3%
2024-10-28 08:00 | 10 | 28 | 8 | 2.962% | 38%
2024-10-28 09:00 | 10 | 28 | 9 | 19.33% | 36.54%
2024-10-28 10:00 | 10 | 28 | 10 | 39.21% | 35.44%
2024-10-28 11:00 | 10 | 28 | 11 | 46.51% | 34.75%
2024-10-28 12:00 | 10 | 28 | 12 | 46.24% | 34.24%
2024-10-28 13:00 | 10 | 28 | 13 | 39.87% | 33.69%
2024-10-28 14:00 | 10 | 28 | 14 | 27.38% | 32.73%
2024-10-28 15:00 | 10 | 28 | 15 | 10.18% | 32.48%
2024-10-28 16:00 | 10 | 28 | 16 | 0% | 32.95%
2024-10-28 17:00 | 10 | 28 | 17 | 0% | 33.91%
2024-10-28 18:00 | 10 | 28 | 18 | 0% | 34.76%
2024-10-28 19:00 | 10 | 28 | 19 | 0% | 35.28%
2024-10-28 20:00 | 10 | 28 | 20 | 0% | 35.29%
2024-10-28 21:00 | 10 | 28 | 21 | 0% | 34.85%
2024-10-28 22:00 | 10 | 28 | 22 | 0% | 34.58%
2024-10-28 23:00 | 10 | 28 | 23 | 0% | 33.69%
2024-10-29 | 10 | 29 | 0 | 0% | 41.22%
2024-10-29 01:00 | 10 | 29 | 1 | 0% | 34.91%
2024-10-29 02:00 | 10 | 29 | 2 | 0% | 35.32%
2024-10-29 03:00 | 10 | 29 | 3 | 0% | 36.44%
2024-10-29 04:00 | 10 | 29 | 4 | 0% | 37.24%
2024-10-29 05:00 | 10 | 29 | 5 | 0% | 37.56%
2024-10-29 06:00 | 10 | 29 | 6 | 0% | 37.65%
2024-10-29 07:00 | 10 | 29 | 7 | 1.16% | 37.4%
2024-10-29 08:00 | 10 | 29 | 8 | 4.55% | 36.72%
2024-10-29 09:00 | 10 | 29 | 9 | 26.21% | 35.63%
2024-10-29 10:00 | 10 | 29 | 10 | 43.19% | 35.41%
2024-10-29 11:00 | 10 | 29 | 11 | 48.7% | 35.65%
2024-10-29 12:00 | 10 | 29 | 12 | 47.7% | 36.06%
2024-10-29 13:00 | 10 | 29 | 13 | 40.64% | 37.26%
2024-10-29 14:00 | 10 | 29 | 14 | 27.13% | 37.8%
2024-10-29 15:00 | 10 | 29 | 15 | 11.68% | 39.33%
2024-10-29 16:00 | 10 | 29 | 16 | 0% | 41.46%
2024-10-29 17:00 | 10 | 29 | 17 | 0% | 43.8%
2024-10-29 18:00 | 10 | 29 | 18 | 0% | 45.24%
2024-10-29 19:00 | 10 | 29 | 19 | 0% | 45.68%
2024-10-29 20:00 | 10 | 29 | 20 | 0% | 45.15%
2024-10-29 21:00 | 10 | 29 | 21 | 0% | 44.28%
2024-10-29 22:00 | 10 | 29 | 22 | 0% | 43.54%
2024-10-29 23:00 | 10 | 29 | 23 | 0% | 43.05%
2024-10-30 | 10 | 30 | 0 | 0% | 35.96%
2024-10-30 01:00 | 10 | 30 | 1 | 0% | 43.19%
2024-10-30 02:00 | 10 | 30 | 2 | 0% | 42.29%
2024-10-30 03:00 | 10 | 30 | 3 | 0% | 38.86%
2024-10-30 04:00 | 10 | 30 | 4 | 0% | 38.29%
2024-10-30 05:00 | 10 | 30 | 5 | 0% | 37.79%
2024-10-30 06:00 | 10 | 30 | 6 | 0% | 37%
2024-10-30 07:00 | 10 | 30 | 7 | 1.315% | 36.54%
2024-10-30 08:00 | 10 | 30 | 8 | 15.02% | 34.84%
2024-10-30 09:00 | 10 | 30 | 9 | 30.12% | 32.02%
2024-10-30 10:00 | 10 | 30 | 10 | 42.83% | 29.88%
2024-10-30 11:00 | 10 | 30 | 11 | 48.48% | 29.07%
2024-10-30 12:00 | 10 | 30 | 12 | 34.2% | 28.98%
2024-10-30 13:00 | 10 | 30 | 13 | 33.1% | 29.34%
2024-10-30 14:00 | 10 | 30 | 14 | 26.5% | 30.98%
2024-10-30 15:00 | 10 | 30 | 15 | 8.58% | 32.53%
2024-10-30 16:00 | 10 | 30 | 16 | 0% | 35.44%
2024-10-30 17:00 | 10 | 30 | 17 | 0% | 37.73%
2024-10-30 18:00 | 10 | 30 | 18 | 0% | 39.55%
2024-10-30 19:00 | 10 | 30 | 19 | 0% | 40.61%
2024-10-30 20:00 | 10 | 30 | 20 | 0% | 40.77%
2024-10-30 21:00 | 10 | 30 | 21 | 0% | 39.97%
2024-10-30 22:00 | 10 | 30 | 22 | 0% | 39.48%
2024-10-30 23:00 | 10 | 30 | 23 | 0% | 37.55%
2024-10-31 | 10 | 31 | 0 | 0% | 38.37%
2024-10-31 01:00 | 10 | 31 | 1 | 0% | 35.45%
2024-10-31 02:00 | 10 | 31 | 2 | 0% | 35.12%
2024-10-31 03:00 | 10 | 31 | 3 | 0% | 35.14%
2024-10-31 04:00 | 10 | 31 | 4 | 0% | 35.65%
2024-10-31 05:00 | 10 | 31 | 5 | 0% | 34.98%
2024-10-31 06:00 | 10 | 31 | 6 | 0% | 34.65%
2024-10-31 07:00 | 10 | 31 | 7 | 0.6018% | 34.4%
2024-10-31 08:00 | 10 | 31 | 8 | 4.157% | 33.58%
2024-10-31 09:00 | 10 | 31 | 9 | 8.005% | 32.98%
2024-10-31 10:00 | 10 | 31 | 10 | 13.33% | 32.71%
2024-10-31 11:00 | 10 | 31 | 11 | 12.2% | 32.24%
2024-10-31 12:00 | 10 | 31 | 12 | 11.8% | 31.49%
2024-10-31 13:00 | 10 | 31 | 13 | 10.57% | 31.48%
2024-10-31 14:00 | 10 | 31 | 14 | 5.474% | 31.99%
2024-10-31 15:00 | 10 | 31 | 15 | 1.677% | 32.4%
2024-10-31 16:00 | 10 | 31 | 16 | 0% | 33.82%
2024-10-31 17:00 | 10 | 31 | 17 | 0% | 34.73%
2024-10-31 18:00 | 10 | 31 | 18 | 0% | 35.74%
2024-10-31 19:00 | 10 | 31 | 19 | 0% | 36.21%
2024-10-31 20:00 | 10 | 31 | 20 | 0% | 36.49%
2024-10-31 21:00 | 10 | 31 | 21 | 0% | 36.76%
2024-10-31 22:00 | 10 | 31 | 22 | 0% | 37.06%
2024-10-31 23:00 | 10 | 31 | 23 | 0% | 40%
2024-11-01 | 11 | 1 | 0 | 0% | 47.16%
2024-11-01 01:00 | 11 | 1 | 1 | 0% | 38.57%
2024-11-01 02:00 | 11 | 1 | 2 | 0% | 38.6%
2024-11-01 03:00 | 11 | 1 | 3 | 0% | 38.6%
2024-11-01 04:00 | 11 | 1 | 4 | 0% | 38.55%
2024-11-01 05:00 | 11 | 1 | 5 | 0% | 38.55%
2024-11-01 06:00 | 11 | 1 | 6 | 0% | 38.72%
2024-11-01 07:00 | 11 | 1 | 7 | 0.1986% | 38.42%
2024-11-01 08:00 | 11 | 1 | 8 | 2.123% | 37.8%
2024-11-01 09:00 | 11 | 1 | 9 | 3.233% | 37.17%
2024-11-01 10:00 | 11 | 1 | 10 | 5.899% | 36.5%
2024-11-01 11:00 | 11 | 1 | 11 | 7.136% | 36.19%
2024-11-01 12:00 | 11 | 1 | 12 | 4.749% | 36.15%
2024-11-01 13:00 | 11 | 1 | 13 | 7.421% | 36.87%
2024-11-01 14:00 | 11 | 1 | 14 | 7.4% | 38.24%
2024-11-01 15:00 | 11 | 1 | 15 | 3.442% | 40.64%
2024-11-01 16:00 | 11 | 1 | 16 | 0% | 43.16%
2024-11-01 17:00 | 11 | 1 | 17 | 0% | 45.32%
2024-11-01 18:00 | 11 | 1 | 18 | 0% | 47.47%
2024-11-01 19:00 | 11 | 1 | 19 | 0% | 48.37%
2024-11-01 20:00 | 11 | 1 | 20 | 0% | 48.99%
2024-11-01 21:00 | 11 | 1 | 21 | 0% | 48.77%
2024-11-01 22:00 | 11 | 1 | 22 | 0% | 48.47%
2024-11-01 23:00 | 11 | 1 | 23 | 0% | 47.6%
2024-11-02 | 11 | 2 | 0 | 0% | 40.35%
2024-11-02 01:00 | 11 | 2 | 1 | 0% | 46.59%
2024-11-02 02:00 | 11 | 2 | 2 | 0% | 46.12%
2024-11-02 03:00 | 11 | 2 | 3 | 0% | 45.08%
2024-11-02 04:00 | 11 | 2 | 4 | 0% | 43.95%
2024-11-02 05:00 | 11 | 2 | 5 | 0% | 43.07%
2024-11-02 06:00 | 11 | 2 | 6 | 0% | 42.16%
2024-11-02 07:00 | 11 | 2 | 7 | 0% | 41.65%
2024-11-02 08:00 | 11 | 2 | 8 | 1.296% | 40.06%
2024-11-02 09:00 | 11 | 2 | 9 | 2.45% | 38.77%
2024-11-02 10:00 | 11 | 2 | 10 | 3.37% | 37.65%
2024-11-02 11:00 | 11 | 2 | 11 | 3.831% | 37.16%
2024-11-02 12:00 | 11 | 2 | 12 | 3.54% | 36.26%
2024-11-02 13:00 | 11 | 2 | 13 | 4.159% | 35.79%
2024-11-02 14:00 | 11 | 2 | 14 | 2.769% | 36.12%
2024-11-02 15:00 | 11 | 2 | 15 | 1.141% | 36.84%
2024-11-02 16:00 | 11 | 2 | 16 | 0% | 38.17%
2024-11-02 17:00 | 11 | 2 | 17 | 0% | 39.76%
2024-11-02 18:00 | 11 | 2 | 18 | 0% | 41.46%
2024-11-02 19:00 | 11 | 2 | 19 | 0% | 42.37%
2024-11-02 20:00 | 11 | 2 | 20 | 0% | 42.57%
2024-11-02 21:00 | 11 | 2 | 21 | 0% | 42.17%
2024-11-02 22:00 | 11 | 2 | 22 | 0% | 41.79%
2024-11-02 23:00 | 11 | 2 | 23 | 0% | 41.14%
2024-11-03 | 11 | 3 | 0 | 0% | 36.37%
2024-11-03 01:00 | 11 | 3 | 1 | 0% | 39.91%
2024-11-03 02:00 | 11 | 3 | 2 | 0% | 39.9%
2024-11-03 03:00 | 11 | 3 | 3 | 0% | 40.23%
2024-11-03 04:00 | 11 | 3 | 4 | 0% | 41.2%
2024-11-03 05:00 | 11 | 3 | 5 | 0% | 41.56%
2024-11-03 06:00 | 11 | 3 | 6 | 0% | 42.32%
2024-11-03 07:00 | 11 | 3 | 7 | 0% | 42.68%
2024-11-03 08:00 | 11 | 3 | 8 | 1.528% | 42.52%
2024-11-03 09:00 | 11 | 3 | 9 | 2.372% | 41.97%
2024-11-03 10:00 | 11 | 3 | 10 | 4.084% | 41.59%
2024-11-03 11:00 | 11 | 3 | 11 | 4.135% | 40.72%
2024-11-03 12:00 | 11 | 3 | 12 | 3.855% | 39.99%
2024-11-03 13:00 | 11 | 3 | 13 | 1.417% | 38.75%
2024-11-03 14:00 | 11 | 3 | 14 | 2.484% | 37.9%
2024-11-03 15:00 | 11 | 3 | 15 | 1.267% | 38.08%
2024-11-03 16:00 | 11 | 3 | 16 | 0% | 38.7%
2024-11-03 17:00 | 11 | 3 | 17 | 0% | 38.65%
2024-11-03 18:00 | 11 | 3 | 18 | 0% | 39.6%
2024-11-03 19:00 | 11 | 3 | 19 | 0% | 39.96%
2024-11-03 20:00 | 11 | 3 | 20 | 0% | 40.16%
2024-11-03 21:00 | 11 | 3 | 21 | 0% | 39.81%
2024-11-03 22:00 | 11 | 3 | 22 | 0% | 39.25%
2024-11-03 23:00 | 11 | 3 | 23 | 0% | 38.05%
2024-11-04 | 11 | 4 | 0 | 0% | 37.71%
2024-11-04 01:00 | 11 | 4 | 1 | 0% | 35.05%
2024-11-04 02:00 | 11 | 4 | 2 | 0% | 34.06%
2024-11-04 03:00 | 11 | 4 | 3 | 0% | 33.47%
2024-11-04 04:00 | 11 | 4 | 4 | 0% | 35.24%
2024-11-04 05:00 | 11 | 4 | 5 | 0% | 33.45%
2024-11-04 06:00 | 11 | 4 | 6 | 0% | 34.06%
2024-11-04 07:00 | 11 | 4 | 7 | 0% | 34.93%
2024-11-04 08:00 | 11 | 4 | 8 | 3.401% | 36.74%
2024-11-04 09:00 | 11 | 4 | 9 | 7.128% | 34.11%
2024-11-04 10:00 | 11 | 4 | 10 | 10.85% | 33.94%
2024-11-04 11:00 | 11 | 4 | 11 | 12.18% | 33.84%
2024-11-04 12:00 | 11 | 4 | 12 | 7.241% | 34.02%
2024-11-04 13:00 | 11 | 4 | 13 | 8.361% | 34.29%
2024-11-04 14:00 | 11 | 4 | 14 | 4.854% | 35.84%
2024-11-04 15:00 | 11 | 4 | 15 | 1.621% | 36.19%
2024-11-04 16:00 | 11 | 4 | 16 | 0% | 38.21%
2024-11-04 17:00 | 11 | 4 | 17 | 0% | 39.73%
2024-11-04 18:00 | 11 | 4 | 18 | 0% | 41.33%
2024-11-04 19:00 | 11 | 4 | 19 | 0% | 41.82%
2024-11-04 20:00 | 11 | 4 | 20 | 0% | 40.83%
2024-11-04 21:00 | 11 | 4 | 21 | 0% | 40.42%
2024-11-04 22:00 | 11 | 4 | 22 | 0% | 38.91%
2024-11-04 23:00 | 11 | 4 | 23 | 0% | 38.21%
2024-11-05 | 11 | 5 | 0 | 0% | 34.56%
2024-11-05 01:00 | 11 | 5 | 1 | 0% | 37.42%
2024-11-05 02:00 | 11 | 5 | 2 | 0% | 37.37%
2024-11-05 03:00 | 11 | 5 | 3 | 0% | 36.88%
2024-11-05 04:00 | 11 | 5 | 4 | 0% | 36.8%
2024-11-05 05:00 | 11 | 5 | 5 | 0% | 37.72%
2024-11-05 06:00 | 11 | 5 | 6 | 0% | 38.68%
2024-11-05 07:00 | 11 | 5 | 7 | 0% | 38.83%
2024-11-05 08:00 | 11 | 5 | 8 | 5.882% | 37.74%
2024-11-05 09:00 | 11 | 5 | 9 | 18.87% | 37.07%
2024-11-05 10:00 | 11 | 5 | 10 | 27.55% | 36.39%
2024-11-05 11:00 | 11 | 5 | 11 | 25.61% | 35.5%
2024-11-05 12:00 | 11 | 5 | 12 | 18.28% | 34.68%
2024-11-05 13:00 | 11 | 5 | 13 | 16.39% | 34.46%
2024-11-05 14:00 | 11 | 5 | 14 | 11.3% | 34.91%
2024-11-05 15:00 | 11 | 5 | 15 | 1.296% | 36.06%
2024-11-05 16:00 | 11 | 5 | 16 | 0% | 37.21%
2024-11-05 17:00 | 11 | 5 | 17 | 0% | 37.86%
2024-11-05 18:00 | 11 | 5 | 18 | 0% | 38.07%
2024-11-05 19:00 | 11 | 5 | 19 | 0% | 37.8%
2024-11-05 20:00 | 11 | 5 | 20 | 0% | 37.35%
2024-11-05 21:00 | 11 | 5 | 21 | 0% | 39.98%
2024-11-05 22:00 | 11 | 5 | 22 | 0% | 33.75%
2024-11-05 23:00 | 11 | 5 | 23 | 0% | 35.46%
2024-11-06 | 11 | 6 | 0 | 0% | 25.49%
2024-11-06 01:00 | 11 | 6 | 1 | 0% | 34.11%
2024-11-06 02:00 | 11 | 6 | 2 | 0% | 36.78%
2024-11-06 03:00 | 11 | 6 | 3 | 0% | 33.47%
2024-11-06 04:00 | 11 | 6 | 4 | 0% | 33.03%
2024-11-06 05:00 | 11 | 6 | 5 | 0% | 32.9%
2024-11-06 06:00 | 11 | 6 | 6 | 0% | 33.26%
2024-11-06 07:00 | 11 | 6 | 7 | 0% | 32.89%
2024-11-06 08:00 | 11 | 6 | 8 | 0% | 32.08%
2024-11-06 09:00 | 11 | 6 | 9 | 1.065% | 30.94%
2024-11-06 10:00 | 11 | 6 | 10 | 3.51% | 29.16%
2024-11-06 11:00 | 11 | 6 | 11 | 6.455% | 27.33%
2024-11-06 12:00 | 11 | 6 | 12 | 4.725% | 25.69%
2024-11-06 13:00 | 11 | 6 | 13 | 3.101% | 24.71%
2024-11-06 14:00 | 11 | 6 | 14 | 1.234% | 23.99%
2024-11-06 15:00 | 11 | 6 | 15 | 0.2381% | 24.06%
2024-11-06 16:00 | 11 | 6 | 16 | 0% | 24.68%
2024-11-06 17:00 | 11 | 6 | 17 | 0% | 25.22%
2024-11-06 18:00 | 11 | 6 | 18 | 0% | 25.35%
2024-11-06 19:00 | 11 | 6 | 19 | 0% | 24.99%
2024-11-06 20:00 | 11 | 6 | 20 | 0% | 24.85%
2024-11-06 21:00 | 11 | 6 | 21 | 0% | 24.85%
2024-11-06 22:00 | 11 | 6 | 22 | 0% | 24.91%
2024-11-06 23:00 | 11 | 6 | 23 | 0% | 25.26%
2024-11-07 | 11 | 7 | 0 | 0% | 23.23%
2024-11-07 01:00 | 11 | 7 | 1 | 0% | 26.32%
2024-11-07 02:00 | 11 | 7 | 2 | 0% | 27.38%
2024-11-07 03:00 | 11 | 7 | 3 | 0% | 28.25%
2024-11-07 04:00 | 11 | 7 | 4 | 0% | 29.02%
2024-11-07 05:00 | 11 | 7 | 5 | 0% | 29.53%
2024-11-07 06:00 | 11 | 7 | 6 | 0% | 30.34%
2024-11-07 07:00 | 11 | 7 | 7 | 0% | 30.48%
2024-11-07 08:00 | 11 | 7 | 8 | 1.541% | 30.14%
2024-11-07 09:00 | 11 | 7 | 9 | 1.902% | 29.15%
2024-11-07 10:00 | 11 | 7 | 10 | 3.323% | 28.24%
2024-11-07 11:00 | 11 | 7 | 11 | 4.367% | 26.88%
2024-11-07 12:00 | 11 | 7 | 12 | 4.863% | 25.74%
2024-11-07 13:00 | 11 | 7 | 13 | 4.247% | 25.22%
2024-11-07 14:00 | 11 | 7 | 14 | 2.854% | 24.76%
2024-11-07 15:00 | 11 | 7 | 15 | 1.476% | 25.01%
2024-11-07 16:00 | 11 | 7 | 16 | 0% | 25%
2024-11-07 17:00 | 11 | 7 | 17 | 0% | 25.27%
2024-11-07 18:00 | 11 | 7 | 18 | 0% | 25.64%
2024-11-07 19:00 | 11 | 7 | 19 | 0% | 25.14%
2024-11-07 20:00 | 11 | 7 | 20 | 0% | 24.53%
2024-11-07 21:00 | 11 | 7 | 21 | 0% | 24.28%
2024-11-07 22:00 | 11 | 7 | 22 | 0% | 24.07%
2024-11-07 23:00 | 11 | 7 | 23 | 0% | 23.75%
2024-11-08 | 11 | 8 | 0 | 0% | 20.78%
2024-11-08 01:00 | 11 | 8 | 1 | 0% | 22.77%
2024-11-08 02:00 | 11 | 8 | 2 | 0% | 21.67%
2024-11-08 03:00 | 11 | 8 | 3 | 0% | 20.55%
2024-11-08 04:00 | 11 | 8 | 4 | 0% | 19.74%
2024-11-08 05:00 | 11 | 8 | 5 | 0% | 19.79%
2024-11-08 06:00 | 11 | 8 | 6 | 0% | 19.77%
2024-11-08 07:00 | 11 | 8 | 7 | 0% | 19.64%
2024-11-08 08:00 | 11 | 8 | 8 | 1.416% | 18.67%
2024-11-08 09:00 | 11 | 8 | 9 | 2.431% | 17.56%
2024-11-08 10:00 | 11 | 8 | 10 | 2.75% | 16.46%
2024-11-08 11:00 | 11 | 8 | 11 | 2.726% | 15.38%
2024-11-08 12:00 | 11 | 8 | 12 | 3.416% | 14.94%
2024-11-08 13:00 | 11 | 8 | 13 | 3.051% | 14.66%
2024-11-08 14:00 | 11 | 8 | 14 | 3.692% | 14.53%
2024-11-08 15:00 | 11 | 8 | 15 | 1.276% | 15%
2024-11-08 16:00 | 11 | 8 | 16 | 0% | 15.89%
2024-11-08 17:00 | 11 | 8 | 17 | 0% | 16.32%
2024-11-08 18:00 | 11 | 8 | 18 | 0% | 16.86%
2024-11-08 19:00 | 11 | 8 | 19 | 0% | 16.96%
2024-11-08 20:00 | 11 | 8 | 20 | 0% | 17.57%
2024-11-08 21:00 | 11 | 8 | 21 | 0% | 18.09%
2024-11-08 22:00 | 11 | 8 | 22 | 0% | 18.41%
2024-11-08 23:00 | 11 | 8 | 23 | 0% | 19.6%
2024-11-09 | 11 | 9 | 0 | 0% | 30.42%
2024-11-09 01:00 | 11 | 9 | 1 | 0% | 23.74%
2024-11-09 02:00 | 11 | 9 | 2 | 0% | 22.63%
2024-11-09 03:00 | 11 | 9 | 3 | 0% | 23.96%
2024-11-09 04:00 | 11 | 9 | 4 | 0% | 25.26%
2024-11-09 05:00 | 11 | 9 | 5 | 0% | 26.68%
2024-11-09 06:00 | 11 | 9 | 6 | 0% | 27.88%
2024-11-09 07:00 | 11 | 9 | 7 | 0% | 28.61%
2024-11-09 08:00 | 11 | 9 | 8 | 1.211% | 28.84%
2024-11-09 09:00 | 11 | 9 | 9 | 2.333% | 32.02%
2024-11-09 10:00 | 11 | 9 | 10 | 2.751% | 29.85%
2024-11-09 11:00 | 11 | 9 | 11 | 6.915% | 29.91%
2024-11-09 12:00 | 11 | 9 | 12 | 16.1% | 29.82%
2024-11-09 13:00 | 11 | 9 | 13 | 4.086% | 29.79%
2024-11-09 14:00 | 11 | 9 | 14 | 1.832% | 29.44%
2024-11-09 15:00 | 11 | 9 | 15 | 1.556% | 29.52%
2024-11-09 16:00 | 11 | 9 | 16 | 0% | 29.64%
2024-11-09 17:00 | 11 | 9 | 17 | 0% | 29.91%
2024-11-09 18:00 | 11 | 9 | 18 | 0% | 30.32%
2024-11-09 19:00 | 11 | 9 | 19 | 0% | 30.52%
2024-11-09 20:00 | 11 | 9 | 20 | 0% | 30.2%
2024-11-09 21:00 | 11 | 9 | 21 | 0% | 29.66%
2024-11-09 22:00 | 11 | 9 | 22 | 0% | 29.6%
2024-11-09 23:00 | 11 | 9 | 23 | 0% | 29.4%
2024-11-10 | 11 | 10 | 0 | 0% | 27.27%
2024-11-10 01:00 | 11 | 10 | 1 | 0% | 28.58%
2024-11-10 02:00 | 11 | 10 | 2 | 0% | 28.35%
2024-11-10 03:00 | 11 | 10 | 3 | 0% | 28.15%
2024-11-10 04:00 | 11 | 10 | 4 | 0% | 28.14%
2024-11-10 05:00 | 11 | 10 | 5 | 0% | 28.03%
2024-11-10 06:00 | 11 | 10 | 6 | 0% | 27.92%
2024-11-10 07:00 | 11 | 10 | 7 | 0% | 27.28%
2024-11-10 08:00 | 11 | 10 | 8 | 1.988% | 26.05%
2024-11-10 09:00 | 11 | 10 | 9 | 14.89% | 25.05%
2024-11-10 10:00 | 11 | 10 | 10 | 29.48% | 24.06%
2024-11-10 11:00 | 11 | 10 | 11 | 34.96% | 23.33%
2024-11-10 12:00 | 11 | 10 | 12 | 34.8% | 22.73%
2024-11-10 13:00 | 11 | 10 | 13 | 28.7% | 22.48%
2024-11-10 14:00 | 11 | 10 | 14 | 17.53% | 22.79%
2024-11-10 15:00 | 11 | 10 | 15 | 3.365% | 23.63%
2024-11-10 16:00 | 11 | 10 | 16 | 0% | 24.66%
2024-11-10 17:00 | 11 | 10 | 17 | 0% | 25.61%
2024-11-10 18:00 | 11 | 10 | 18 | 0% | 26.32%
2024-11-10 19:00 | 11 | 10 | 19 | 0% | 26.59%
2024-11-10 20:00 | 11 | 10 | 20 | 0% | 26.86%
2024-11-10 21:00 | 11 | 10 | 21 | 0% | 27.02%
2024-11-10 22:00 | 11 | 10 | 22 | 0% | 26.99%
2024-11-10 23:00 | 11 | 10 | 23 | 0% | 27.09%
2024-11-11 | 11 | 11 | 0 | 0% | 34.7%
2024-11-11 01:00 | 11 | 11 | 1 | 0% | 27.92%
2024-11-11 02:00 | 11 | 11 | 2 | 0% | 28.49%
2024-11-11 03:00 | 11 | 11 | 3 | 0% | 28.81%
2024-11-11 04:00 | 11 | 11 | 4 | 0% | 29.2%
2024-11-11 05:00 | 11 | 11 | 5 | 0% | 30.41%
2024-11-11 06:00 | 11 | 11 | 6 | 0% | 31.42%
2024-11-11 07:00 | 11 | 11 | 7 | 0% | 32.04%
2024-11-11 08:00 | 11 | 11 | 8 | 6.569% | 32.13%
2024-11-11 09:00 | 11 | 11 | 9 | 20.81% | 32.34%
2024-11-11 10:00 | 11 | 11 | 10 | 30.3% | 31.89%
2024-11-11 11:00 | 11 | 11 | 11 | 35.3% | 31.56%
2024-11-11 12:00 | 11 | 11 | 12 | 34.96% | 31.38%
2024-11-11 13:00 | 11 | 11 | 13 | 28.94% | 31%
2024-11-11 14:00 | 11 | 11 | 14 | 18.27% | 31.11%
2024-11-11 15:00 | 11 | 11 | 15 | 3.898% | 30.93%
2024-11-11 16:00 | 11 | 11 | 16 | 0% | 32.83%
2024-11-11 17:00 | 11 | 11 | 17 | 0% | 33.4%
2024-11-11 18:00 | 11 | 11 | 18 | 0% | 34.34%
2024-11-11 19:00 | 11 | 11 | 19 | 0% | 34.89%
2024-11-11 20:00 | 11 | 11 | 20 | 0% | 35.33%
2024-11-11 21:00 | 11 | 11 | 21 | 0% | 35.66%
2024-11-11 22:00 | 11 | 11 | 22 | 0% | 35.25%
2024-11-11 23:00 | 11 | 11 | 23 | 0% | 34.67%
2024-11-12 | 11 | 12 | 0 | 0% | 26.74%
2024-11-12 01:00 | 11 | 12 | 1 | 0% | 34.77%
2024-11-12 02:00 | 11 | 12 | 2 | 0% | 35.05%
2024-11-12 03:00 | 11 | 12 | 3 | 0% | 35.71%
2024-11-12 04:00 | 11 | 12 | 4 | 0% | 36.33%
2024-11-12 05:00 | 11 | 12 | 5 | 0% | 36.68%
2024-11-12 06:00 | 11 | 12 | 6 | 0% | 37.98%
2024-11-12 07:00 | 11 | 12 | 7 | 0% | 37.35%
2024-11-12 08:00 | 11 | 12 | 8 | 5.537% | 37.38%
2024-11-12 09:00 | 11 | 12 | 9 | 19.19% | 36.7%
2024-11-12 10:00 | 11 | 12 | 10 | 29.24% | 35.35%
2024-11-12 11:00 | 11 | 12 | 11 | 34.58% | 34.02%
2024-11-12 12:00 | 11 | 12 | 12 | 34.31% | 32.48%
2024-11-12 13:00 | 11 | 12 | 13 | 28.12% | 31.74%
2024-11-12 14:00 | 11 | 12 | 14 | 17.33% | 33.77%
2024-11-12 15:00 | 11 | 12 | 15 | 3.403% | 31.9%
2024-11-12 16:00 | 11 | 12 | 16 | 0% | 32.51%
2024-11-12 17:00 | 11 | 12 | 17 | 0% | 32.94%
2024-11-12 18:00 | 11 | 12 | 18 | 0% | 32.53%
2024-11-12 19:00 | 11 | 12 | 19 | 0% | 33.94%
2024-11-12 20:00 | 11 | 12 | 20 | 0% | 30.44%
2024-11-12 21:00 | 11 | 12 | 21 | 0% | 29.75%
2024-11-12 22:00 | 11 | 12 | 22 | 0% | 29.11%
2024-11-12 23:00 | 11 | 12 | 23 | 0% | 28.01%
2024-11-13 | 11 | 13 | 0 | 0% | 21.3%
2024-11-13 01:00 | 11 | 13 | 1 | 0% | 26.57%
2024-11-13 02:00 | 11 | 13 | 2 | 0% | 26.92%
2024-11-13 03:00 | 11 | 13 | 3 | 0% | 26.77%
2024-11-13 04:00 | 11 | 13 | 4 | 0% | 27.74%
2024-11-13 05:00 | 11 | 13 | 5 | 0% | 28.4%
2024-11-13 06:00 | 11 | 13 | 6 | 0% | 29.38%
2024-11-13 07:00 | 11 | 13 | 7 | 0% | 29.22%
2024-11-13 08:00 | 11 | 13 | 8 | 1.192% | 28.77%
2024-11-13 09:00 | 11 | 13 | 9 | 1.955% | 27.28%
2024-11-13 10:00 | 11 | 13 | 10 | 4.028% | 25.23%
2024-11-13 11:00 | 11 | 13 | 11 | 6.356% | 23.27%
2024-11-13 12:00 | 11 | 13 | 12 | 5.703% | 21.71%
2024-11-13 13:00 | 11 | 13 | 13 | 5.562% | 20.75%
2024-11-13 14:00 | 11 | 13 | 14 | 1.348% | 20.35%
2024-11-13 15:00 | 11 | 13 | 15 | 0% | 21.4%
2024-11-13 16:00 | 11 | 13 | 16 | 0% | 22.33%
2024-11-13 17:00 | 11 | 13 | 17 | 0% | 23.19%
2024-11-13 18:00 | 11 | 13 | 18 | 0% | 23.41%
2024-11-13 19:00 | 11 | 13 | 19 | 0% | 23.23%
2024-11-13 20:00 | 11 | 13 | 20 | 0% | 22.32%
2024-11-13 21:00 | 11 | 13 | 21 | 0% | 21.16%
2024-11-13 22:00 | 11 | 13 | 22 | 0% | 20.91%
2024-11-13 23:00 | 11 | 13 | 23 | 0% | 21.05%
2024-11-14 | 11 | 14 | 0 | 0% | 32.2%
2024-11-14 01:00 | 11 | 14 | 1 | 0% | 21.88%
2024-11-14 02:00 | 11 | 14 | 2 | 0% | 22.66%
2024-11-14 03:00 | 11 | 14 | 3 | 0% | 22.95%
2024-11-14 04:00 | 11 | 14 | 4 | 0% | 24.1%
2024-11-14 05:00 | 11 | 14 | 5 | 0% | 23.39%
2024-11-14 06:00 | 11 | 14 | 6 | 0% | 23.63%
2024-11-14 07:00 | 11 | 14 | 7 | 0% | 23.2%
2024-11-14 08:00 | 11 | 14 | 8 | 1.666% | 22.83%
2024-11-14 09:00 | 11 | 14 | 9 | 3.902% | 22.56%
2024-11-14 10:00 | 11 | 14 | 10 | 4.02% | 21.6%
2024-11-14 11:00 | 11 | 14 | 11 | 6.589% | 20.94%
2024-11-14 12:00 | 11 | 14 | 12 | 10.14% | 20.78%
2024-11-14 13:00 | 11 | 14 | 13 | 6.172% | 21.16%
2024-11-14 14:00 | 11 | 14 | 14 | 2.191% | 21.75%
2024-11-14 15:00 | 11 | 14 | 15 | 1.783% | 22.97%
2024-11-14 16:00 | 11 | 14 | 16 | 0% | 24.86%
2024-11-14 17:00 | 11 | 14 | 17 | 0% | 27.09%
2024-11-14 18:00 | 11 | 14 | 18 | 0% | 29.48%
2024-11-14 19:00 | 11 | 14 | 19 | 0% | 31.13%
2024-11-14 20:00 | 11 | 14 | 20 | 0% | 32.09%
2024-11-14 21:00 | 11 | 14 | 21 | 0% | 32.41%
2024-11-14 22:00 | 11 | 14 | 22 | 0% | 32.58%
2024-11-14 23:00 | 11 | 14 | 23 | 0% | 32.35%
2024-11-15 | 11 | 15 | 0 | 0% | 41.86%
2024-11-15 01:00 | 11 | 15 | 1 | 0% | 32.75%
2024-11-15 02:00 | 11 | 15 | 2 | 0% | 33.34%
2024-11-15 03:00 | 11 | 15 | 3 | 0% | 34.08%
2024-11-15 04:00 | 11 | 15 | 4 | 0% | 34.07%
2024-11-15 05:00 | 11 | 15 | 5 | 0% | 34.46%
2024-11-15 06:00 | 11 | 15 | 6 | 0% | 34.82%
2024-11-15 07:00 | 11 | 15 | 7 | 0% | 35.42%
2024-11-15 08:00 | 11 | 15 | 8 | 4.966% | 35.83%
2024-11-15 09:00 | 11 | 15 | 9 | 18.85% | 36.22%
2024-11-15 10:00 | 11 | 15 | 10 | 28.94% | 36.15%
2024-11-15 11:00 | 11 | 15 | 11 | 33.41% | 35.27%
2024-11-15 12:00 | 11 | 15 | 12 | 28.01% | 34.52%
2024-11-15 13:00 | 11 | 15 | 13 | 14.95% | 35.01%
2024-11-15 14:00 | 11 | 15 | 14 | 8.997% | 35.53%
2024-11-15 15:00 | 11 | 15 | 15 | 1.973% | 37.03%
2024-11-15 16:00 | 11 | 15 | 16 | 0% | 39.8%
2024-11-15 17:00 | 11 | 15 | 17 | 0% | 41.76%
2024-11-15 18:00 | 11 | 15 | 18 | 0% | 42.61%
2024-11-15 19:00 | 11 | 15 | 19 | 0% | 43.31%
2024-11-15 20:00 | 11 | 15 | 20 | 0% | 43.77%
2024-11-15 21:00 | 11 | 15 | 21 | 0% | 43.36%
2024-11-15 22:00 | 11 | 15 | 22 | 0% | 43.24%
2024-11-15 23:00 | 11 | 15 | 23 | 0% | 42.6%
2024-11-16 | 11 | 16 | 0 | 0% | 47.82%
2024-11-16 01:00 | 11 | 16 | 1 | 0% | 42.02%
2024-11-16 02:00 | 11 | 16 | 2 | 0% | 42.77%
2024-11-16 03:00 | 11 | 16 | 3 | 0% | 42.9%
2024-11-16 04:00 | 11 | 16 | 4 | 0% | 43%
2024-11-16 05:00 | 11 | 16 | 5 | 0% | 42.53%
2024-11-16 06:00 | 11 | 16 | 6 | 0% | 42.69%
2024-11-16 07:00 | 11 | 16 | 7 | 0% | 43%
2024-11-16 08:00 | 11 | 16 | 8 | 1.669% | 43.41%
2024-11-16 09:00 | 11 | 16 | 9 | 16.27% | 41.79%
2024-11-16 10:00 | 11 | 16 | 10 | 24.13% | 41.12%
2024-11-16 11:00 | 11 | 16 | 11 | 25.35% | 40.81%
2024-11-16 12:00 | 11 | 16 | 12 | 22.59% | 40.46%
2024-11-16 13:00 | 11 | 16 | 13 | 17.49% | 40.83%
2024-11-16 14:00 | 11 | 16 | 14 | 7.941% | 42.58%
2024-11-16 15:00 | 11 | 16 | 15 | 2.592% | 44.39%
2024-11-16 16:00 | 11 | 16 | 16 | 0% | 46.7%
2024-11-16 17:00 | 11 | 16 | 17 | 0% | 47.96%
2024-11-16 18:00 | 11 | 16 | 18 | 0% | 48.77%
2024-11-16 19:00 | 11 | 16 | 19 | 0% | 48.93%
2024-11-16 20:00 | 11 | 16 | 20 | 0% | 48.76%
2024-11-16 21:00 | 11 | 16 | 21 | 0% | 47.96%
2024-11-16 22:00 | 11 | 16 | 22 | 0% | 47.72%
2024-11-16 23:00 | 11 | 16 | 23 | 0% | 47.55%
2024-11-17 | 11 | 17 | 0 | 0% | 35.07%
2024-11-17 01:00 | 11 | 17 | 1 | 0% | 47.71%
2024-11-17 02:00 | 11 | 17 | 2 | 0% | 46.66%
2024-11-17 03:00 | 11 | 17 | 3 | 0% | 46.41%
2024-11-17 04:00 | 11 | 17 | 4 | 0% | 44.45%
2024-11-17 05:00 | 11 | 17 | 5 | 0% | 45.17%
2024-11-17 06:00 | 11 | 17 | 6 | 0% | 44.5%
2024-11-17 07:00 | 11 | 17 | 7 | 0% | 43.95%
2024-11-17 08:00 | 11 | 17 | 8 | 0.6899% | 42.56%
2024-11-17 09:00 | 11 | 17 | 9 | 1.075% | 41.4%
2024-11-17 10:00 | 11 | 17 | 10 | 1.239% | 40.34%
2024-11-17 11:00 | 11 | 17 | 11 | 1.877% | 39.11%
2024-11-17 12:00 | 11 | 17 | 12 | 1.688% | 38.23%
2024-11-17 13:00 | 11 | 17 | 13 | 1.144% | 37.59%
2024-11-17 14:00 | 11 | 17 | 14 | 0.793% | 37.4%
2024-11-17 15:00 | 11 | 17 | 15 | 0% | 38.33%
2024-11-17 16:00 | 11 | 17 | 16 | 0% | 39.89%
2024-11-17 17:00 | 11 | 17 | 17 | 0% | 40.34%
2024-11-17 18:00 | 11 | 17 | 18 | 0% | 40.4%
2024-11-17 19:00 | 11 | 17 | 19 | 0% | 39.69%
2024-11-17 20:00 | 11 | 17 | 20 | 0% | 38.7%
2024-11-17 21:00 | 11 | 17 | 21 | 0% | 37.38%
2024-11-17 22:00 | 11 | 17 | 22 | 0% | 32.01%
2024-11-17 23:00 | 11 | 17 | 23 | 0% | 36.28%
2024-11-18 | 11 | 18 | 0 | 0% | 32.98%
2024-11-18 01:00 | 11 | 18 | 1 | 0% | 35.52%
2024-11-18 02:00 | 11 | 18 | 2 | 0% | 35.78%
2024-11-18 03:00 | 11 | 18 | 3 | 0% | 36.11%
2024-11-18 04:00 | 11 | 18 | 4 | 0% | 35.9%
2024-11-18 05:00 | 11 | 18 | 5 | 0% | 35.5%
2024-11-18 06:00 | 11 | 18 | 6 | 0% | 35.35%
2024-11-18 07:00 | 11 | 18 | 7 | 0% | 34.64%
2024-11-18 08:00 | 11 | 18 | 8 | 0.1956% | 33.6%
2024-11-18 09:00 | 11 | 18 | 9 | 0.5219% | 32.51%
2024-11-18 10:00 | 11 | 18 | 10 | 0.704% | 31.18%
2024-11-18 11:00 | 11 | 18 | 11 | 1.673% | 29.98%
2024-11-18 12:00 | 11 | 18 | 12 | 1.135% | 29.75%
2024-11-18 13:00 | 11 | 18 | 13 | 1.042% | 29.7%
2024-11-18 14:00 | 11 | 18 | 14 | 0.969% | 30.37%
2024-11-18 15:00 | 11 | 18 | 15 | 0% | 30.88%
2024-11-18 16:00 | 11 | 18 | 16 | 0% | 31.88%
2024-11-18 17:00 | 11 | 18 | 17 | 0% | 32.39%
2024-11-18 18:00 | 11 | 18 | 18 | 0% | 33.04%
2024-11-18 19:00 | 11 | 18 | 19 | 0% | 32.68%
2024-11-18 20:00 | 11 | 18 | 20 | 0% | 32.56%
2024-11-18 21:00 | 11 | 18 | 21 | 0% | 31.99%
2024-11-18 22:00 | 11 | 18 | 22 | 0% | 31.73%
2024-11-18 23:00 | 11 | 18 | 23 | 0% | 32.1%
2024-11-19 | 11 | 19 | 0 | 0% | 34.68%
2024-11-19 01:00 | 11 | 19 | 1 | 0% | 33.22%
2024-11-19 02:00 | 11 | 19 | 2 | 0% | 33.47%
2024-11-19 03:00 | 11 | 19 | 3 | 0% | 35.42%
2024-11-19 04:00 | 11 | 19 | 4 | 0% | 35.51%
2024-11-19 05:00 | 11 | 19 | 5 | 0% | 37.33%
2024-11-19 06:00 | 11 | 19 | 6 | 0% | 38.71%
2024-11-19 07:00 | 11 | 19 | 7 | 0% | 39.94%
2024-11-19 08:00 | 11 | 19 | 8 | 0% | 40.72%
2024-11-19 09:00 | 11 | 19 | 9 | 0.507% | 41.12%
2024-11-19 10:00 | 11 | 19 | 10 | 0.7709% | 40.72%
2024-11-19 11:00 | 11 | 19 | 11 | 1.929% | 40.51%
2024-11-19 12:00 | 11 | 19 | 12 | 1.118% | 39.24%
2024-11-19 13:00 | 11 | 19 | 13 | 2.455% | 37.93%
2024-11-19 14:00 | 11 | 19 | 14 | 1.463% | 36.87%
2024-11-19 15:00 | 11 | 19 | 15 | 0% | 36.97%
2024-11-19 16:00 | 11 | 19 | 16 | 0% | 37.44%
2024-11-19 17:00 | 11 | 19 | 17 | 0% | 38.05%
2024-11-19 18:00 | 11 | 19 | 18 | 0% | 37.84%
2024-11-19 19:00 | 11 | 19 | 19 | 0% | 37.19%
2024-11-19 20:00 | 11 | 19 | 20 | 0% | 36.37%
2024-11-19 21:00 | 11 | 19 | 21 | 0% | 35.65%
2024-11-19 22:00 | 11 | 19 | 22 | 0% | 34.98%
2024-11-19 23:00 | 11 | 19 | 23 | 0% | 34.74%
2024-11-20 | 11 | 20 | 0 | 0% | 39.6%
2024-11-20 01:00 | 11 | 20 | 1 | 0% | 34.47%
2024-11-20 02:00 | 11 | 20 | 2 | 0% | 34.52%
2024-11-20 03:00 | 11 | 20 | 3 | 0% | 34.09%
2024-11-20 04:00 | 11 | 20 | 4 | 0% | 34.11%
2024-11-20 05:00 | 11 | 20 | 5 | 0% | 33.91%
2024-11-20 06:00 | 11 | 20 | 6 | 0% | 33.87%
2024-11-20 07:00 | 11 | 20 | 7 | 0% | 33.24%
2024-11-20 08:00 | 11 | 20 | 8 | 0% | 32.54%
2024-11-20 09:00 | 11 | 20 | 9 | 2.965% | 31.59%
2024-11-20 10:00 | 11 | 20 | 10 | 11.91% | 30.28%
2024-11-20 11:00 | 11 | 20 | 11 | 18.87% | 30.25%
2024-11-20 12:00 | 11 | 20 | 12 | 6.41% | 28.2%
2024-11-20 13:00 | 11 | 20 | 13 | 4.347% | 27.82%
2024-11-20 14:00 | 11 | 20 | 14 | 3.057% | 30.74%
2024-11-20 15:00 | 11 | 20 | 15 | 0.8468% | 30.6%
2024-11-20 16:00 | 11 | 20 | 16 | 0% | 32.95%
2024-11-20 17:00 | 11 | 20 | 17 | 0% | 34.59%
2024-11-20 18:00 | 11 | 20 | 18 | 0% | 35.62%
2024-11-20 19:00 | 11 | 20 | 19 | 0% | 36.31%
2024-11-20 20:00 | 11 | 20 | 20 | 0% | 36.76%
2024-11-20 21:00 | 11 | 20 | 21 | 0% | 37.41%
2024-11-20 22:00 | 11 | 20 | 22 | 0% | 38.18%
2024-11-20 23:00 | 11 | 20 | 23 | 0% | 39.06%
2024-11-21 | 11 | 21 | 0 | 0% | 35.45%
2024-11-21 01:00 | 11 | 21 | 1 | 0% | 40.85%
2024-11-21 02:00 | 11 | 21 | 2 | 0% | 41.54%
2024-11-21 03:00 | 11 | 21 | 3 | 0% | 41.87%
2024-11-21 04:00 | 11 | 21 | 4 | 0% | 42.24%
2024-11-21 05:00 | 11 | 21 | 5 | 0% | 42.18%
2024-11-21 06:00 | 11 | 21 | 6 | 0% | 42.47%
2024-11-21 07:00 | 11 | 21 | 7 | 0% | 41.7%
2024-11-21 08:00 | 11 | 21 | 8 | 0% | 40.6%
2024-11-21 09:00 | 11 | 21 | 9 | 1.484% | 38.8%
2024-11-21 10:00 | 11 | 21 | 10 | 1.79% | 36.08%
2024-11-21 11:00 | 11 | 21 | 11 | 1.869% | 33.58%
2024-11-21 12:00 | 11 | 21 | 12 | 1.224% | 31.77%
2024-11-21 13:00 | 11 | 21 | 13 | 1.045% | 30.71%
2024-11-21 14:00 | 11 | 21 | 14 | 0.7871% | 31.01%
2024-11-21 15:00 | 11 | 21 | 15 | 0.3308% | 31.8%
2024-11-21 16:00 | 11 | 21 | 16 | 0% | 32.47%
2024-11-21 17:00 | 11 | 21 | 17 | 0% | 32.82%
2024-11-21 18:00 | 11 | 21 | 18 | 0% | 32.95%
2024-11-21 19:00 | 11 | 21 | 19 | 0% | 33.01%
2024-11-21 20:00 | 11 | 21 | 20 | 0% | 32.77%
2024-11-21 21:00 | 11 | 21 | 21 | 0% | 32.99%
2024-11-21 22:00 | 11 | 21 | 22 | 0% | 33.72%
2024-11-21 23:00 | 11 | 21 | 23 | 0% | 34.81%
2024-11-22 | 11 | 22 | 0 | 0% | 51.09%
2024-11-22 01:00 | 11 | 22 | 1 | 0% | 36.16%
2024-11-22 02:00 | 11 | 22 | 2 | 0% | 37.12%
2024-11-22 03:00 | 11 | 22 | 3 | 0% | 38.68%
2024-11-22 04:00 | 11 | 22 | 4 | 0% | 40.45%
2024-11-22 05:00 | 11 | 22 | 5 | 0% | 42.17%
2024-11-22 06:00 | 11 | 22 | 6 | 0% | 43.97%
2024-11-22 07:00 | 11 | 22 | 7 | 0% | 45.67%
2024-11-22 08:00 | 11 | 22 | 8 | 1.071% | 46.67%
2024-11-22 09:00 | 11 | 22 | 9 | 2.07% | 47.89%
2024-11-22 10:00 | 11 | 22 | 10 | 1.994% | 48.58%
2024-11-22 11:00 | 11 | 22 | 11 | 2.254% | 49%
2024-11-22 12:00 | 11 | 22 | 12 | 3.5% | 50.06%
2024-11-22 13:00 | 11 | 22 | 13 | 3.058% | 51.37%
2024-11-22 14:00 | 11 | 22 | 14 | 1.74% | 51.69%
2024-11-22 15:00 | 11 | 22 | 15 | 0.2981% | 53.04%
2024-11-22 16:00 | 11 | 22 | 16 | 0% | 54.42%
2024-11-22 17:00 | 11 | 22 | 17 | 0% | 54.48%
2024-11-22 18:00 | 11 | 22 | 18 | 0% | 58.3%
2024-11-22 19:00 | 11 | 22 | 19 | 0% | 52.77%
2024-11-22 20:00 | 11 | 22 | 20 | 0% | 51.58%
2024-11-22 21:00 | 11 | 22 | 21 | 0% | 50.82%
2024-11-22 22:00 | 11 | 22 | 22 | 0% | 50.64%
2024-11-22 23:00 | 11 | 22 | 23 | 0% | 54.76%
2024-11-23 | 11 | 23 | 0 | 0% | 44.88%
2024-11-23 01:00 | 11 | 23 | 1 | 0% | 51.24%
2024-11-23 02:00 | 11 | 23 | 2 | 0% | 51.68%
2024-11-23 03:00 | 11 | 23 | 3 | 0% | 51.79%
2024-11-23 04:00 | 11 | 23 | 4 | 0% | 50.51%
2024-11-23 05:00 | 11 | 23 | 5 | 0% | 51.16%
2024-11-23 06:00 | 11 | 23 | 6 | 0% | 52.52%
2024-11-23 07:00 | 11 | 23 | 7 | 0% | 50.12%
2024-11-23 08:00 | 11 | 23 | 8 | 0% | 49.24%
2024-11-23 09:00 | 11 | 23 | 9 | 1.286% | 48.42%
2024-11-23 10:00 | 11 | 23 | 10 | 0.7803% | 47.59%
2024-11-23 11:00 | 11 | 23 | 11 | 1.872% | 46.52%
2024-11-23 12:00 | 11 | 23 | 12 | 1.495% | 45.91%
2024-11-23 13:00 | 11 | 23 | 13 | 0.6943% | 45.25%
2024-11-23 14:00 | 11 | 23 | 14 | 0.8879% | 45.6%
2024-11-23 15:00 | 11 | 23 | 15 | 0% | 46.66%
2024-11-23 16:00 | 11 | 23 | 16 | 0% | 47.37%
2024-11-23 17:00 | 11 | 23 | 17 | 0% | 48.02%
2024-11-23 18:00 | 11 | 23 | 18 | 0% | 48.05%
2024-11-23 19:00 | 11 | 23 | 19 | 0% | 50.47%
2024-11-23 20:00 | 11 | 23 | 20 | 0% | 47.37%
2024-11-23 21:00 | 11 | 23 | 21 | 0% | 46.69%
2024-11-23 22:00 | 11 | 23 | 22 | 0% | 46.03%
2024-11-23 23:00 | 11 | 23 | 23 | 0% | 45.64%
2024-11-24 | 11 | 24 | 0 | 0% | 39.9%
2024-11-24 01:00 | 11 | 24 | 1 | 0% | 44.11%
2024-11-24 02:00 | 11 | 24 | 2 | 0% | 43.1%
2024-11-24 03:00 | 11 | 24 | 3 | 0% | 42.28%
2024-11-24 04:00 | 11 | 24 | 4 | 0% | 41.63%
2024-11-24 05:00 | 11 | 24 | 5 | 0% | 41.06%
2024-11-24 06:00 | 11 | 24 | 6 | 0% | 40.52%
2024-11-24 07:00 | 11 | 24 | 7 | 0% | 40.03%
2024-11-24 08:00 | 11 | 24 | 8 | 0% | 39.14%
2024-11-24 09:00 | 11 | 24 | 9 | 0.5861% | 38.71%
2024-11-24 10:00 | 11 | 24 | 10 | 0.7611% | 37.93%
2024-11-24 11:00 | 11 | 24 | 11 | 1.379% | 37.09%
2024-11-24 12:00 | 11 | 24 | 12 | 2.13% | 36.77%
2024-11-24 13:00 | 11 | 24 | 13 | 1.772% | 37.64%
2024-11-24 14:00 | 11 | 24 | 14 | 1.29% | 39.35%
2024-11-24 15:00 | 11 | 24 | 15 | 0% | 41.19%
2024-11-24 16:00 | 11 | 24 | 16 | 0% | 42.79%
2024-11-24 17:00 | 11 | 24 | 17 | 0% | 43.24%
2024-11-24 18:00 | 11 | 24 | 18 | 0% | 43.16%
2024-11-24 19:00 | 11 | 24 | 19 | 0% | 42.11%
2024-11-24 20:00 | 11 | 24 | 20 | 0% | 41.26%
2024-11-24 21:00 | 11 | 24 | 21 | 0% | 40.65%
2024-11-24 22:00 | 11 | 24 | 22 | 0% | 40.68%
2024-11-24 23:00 | 11 | 24 | 23 | 0% | 40.41%
2024-11-25 | 11 | 25 | 0 | 0% | 28.84%
2024-11-25 01:00 | 11 | 25 | 1 | 0% | 39.97%
2024-11-25 02:00 | 11 | 25 | 2 | 0% | 40.01%
2024-11-25 03:00 | 11 | 25 | 3 | 0% | 40.17%
2024-11-25 04:00 | 11 | 25 | 4 | 0% | 40.59%
2024-11-25 05:00 | 11 | 25 | 5 | 0% | 40.05%
2024-11-25 06:00 | 11 | 25 | 6 | 0% | 39.87%
2024-11-25 07:00 | 11 | 25 | 7 | 0% | 39.4%
2024-11-25 08:00 | 11 | 25 | 8 | 0% | 38.28%
2024-11-25 09:00 | 11 | 25 | 9 | 0.4998% | 36.82%
2024-11-25 10:00 | 11 | 25 | 10 | 0.9379% | 35.26%
2024-11-25 11:00 | 11 | 25 | 11 | 2.23% | 33.69%
2024-11-25 12:00 | 11 | 25 | 12 | 2.034% | 32.88%
2024-11-25 13:00 | 11 | 25 | 13 | 1.39% | 32.27%
2024-11-25 14:00 | 11 | 25 | 14 | 1.651% | 32.07%
2024-11-25 15:00 | 11 | 25 | 15 | 0.2049% | 32.71%
2024-11-25 16:00 | 11 | 25 | 16 | 0% | 33.82%
2024-11-25 17:00 | 11 | 25 | 17 | 0% | 34.58%
2024-11-25 18:00 | 11 | 25 | 18 | 0% | 34.21%
2024-11-25 19:00 | 11 | 25 | 19 | 0% | 33.59%
2024-11-25 20:00 | 11 | 25 | 20 | 0% | 35.4%
2024-11-25 21:00 | 11 | 25 | 21 | 0% | 32.12%
2024-11-25 22:00 | 11 | 25 | 22 | 0% | 31.45%
2024-11-25 23:00 | 11 | 25 | 23 | 0% | 30.3%
2024-11-26 | 11 | 26 | 0 | 0% | 32.56%
2024-11-26 01:00 | 11 | 26 | 1 | 0% | 28.47%
2024-11-26 02:00 | 11 | 26 | 2 | 0% | 27.84%
2024-11-26 03:00 | 11 | 26 | 3 | 0% | 27.02%
2024-11-26 04:00 | 11 | 26 | 4 | 0% | 26.65%
2024-11-26 05:00 | 11 | 26 | 5 | 0% | 27.03%
2024-11-26 06:00 | 11 | 26 | 6 | 0% | 27.17%
2024-11-26 07:00 | 11 | 26 | 7 | 0% | 26.99%
2024-11-26 08:00 | 11 | 26 | 8 | 0.2935% | 26.32%
2024-11-26 09:00 | 11 | 26 | 9 | 2.153% | 27.86%
2024-11-26 10:00 | 11 | 26 | 10 | 2.743% | 24.97%
2024-11-26 11:00 | 11 | 26 | 11 | 6.804% | 24.49%
2024-11-26 12:00 | 11 | 26 | 12 | 6.546% | 23.3%
2024-11-26 13:00 | 11 | 26 | 13 | 2.979% | 23.65%
2024-11-26 14:00 | 11 | 26 | 14 | 0.5036% | 25.14%
2024-11-26 15:00 | 11 | 26 | 15 | 0% | 28.93%
2024-11-26 16:00 | 11 | 26 | 16 | 0% | 28.64%
2024-11-26 17:00 | 11 | 26 | 17 | 0% | 29.64%
2024-11-26 18:00 | 11 | 26 | 18 | 0% | 30.36%
2024-11-26 19:00 | 11 | 26 | 19 | 0% | 31.43%
2024-11-26 20:00 | 11 | 26 | 20 | 0% | 31.95%
2024-11-26 21:00 | 11 | 26 | 21 | 0% | 31.94%
2024-11-26 22:00 | 11 | 26 | 22 | 0% | 32.25%
2024-11-26 23:00 | 11 | 26 | 23 | 0% | 32.07%
2024-11-27 | 11 | 27 | 0 | 0% | 39.89%
2024-11-27 01:00 | 11 | 27 | 1 | 0% | 32.73%
2024-11-27 02:00 | 11 | 27 | 2 | 0% | 30.56%
2024-11-27 03:00 | 11 | 27 | 3 | 0% | 33.72%
2024-11-27 04:00 | 11 | 27 | 4 | 0% | 34.26%
2024-11-27 05:00 | 11 | 27 | 5 | 0% | 34.9%
2024-11-27 06:00 | 11 | 27 | 6 | 0% | 35.3%
2024-11-27 07:00 | 11 | 27 | 7 | 0% | 35.49%
2024-11-27 08:00 | 11 | 27 | 8 | 0% | 35.23%
2024-11-27 09:00 | 11 | 27 | 9 | 1.294% | 32.15%
2024-11-27 10:00 | 11 | 27 | 10 | 0% | 34.31%
2024-11-27 11:00 | 11 | 27 | 11 | 0.6746% | 34.16%
2024-11-27 12:00 | 11 | 27 | 12 | 5.694% | 34.28%
2024-11-27 13:00 | 11 | 27 | 13 | 6.509% | 34.79%
2024-11-27 14:00 | 11 | 27 | 14 | 3.406% | 37.66%
2024-11-27 15:00 | 11 | 27 | 15 | 0% | 36.11%
2024-11-27 16:00 | 11 | 27 | 16 | 0% | 36.79%
2024-11-27 17:00 | 11 | 27 | 17 | 0% | 37.29%
2024-11-27 18:00 | 11 | 27 | 18 | 0% | 37.99%
2024-11-27 19:00 | 11 | 27 | 19 | 0% | 38.42%
2024-11-27 20:00 | 11 | 27 | 20 | 0% | 38.72%
2024-11-27 21:00 | 11 | 27 | 21 | 0% | 38.84%
2024-11-27 22:00 | 11 | 27 | 22 | 0% | 38.95%
2024-11-27 23:00 | 11 | 27 | 23 | 0% | 39.27%
2024-11-28 | 11 | 28 | 0 | 0% | 39.51%
2024-11-28 01:00 | 11 | 28 | 1 | 0% | 40.53%
2024-11-28 02:00 | 11 | 28 | 2 | 0% | 40.67%
2024-11-28 03:00 | 11 | 28 | 3 | 0% | 41.09%
2024-11-28 04:00 | 11 | 28 | 4 | 0% | 41.13%
2024-11-28 05:00 | 11 | 28 | 5 | 0% | 41.57%
2024-11-28 06:00 | 11 | 28 | 6 | 0% | 41.93%
2024-11-28 07:00 | 11 | 28 | 7 | 0% | 41.88%
2024-11-28 08:00 | 11 | 28 | 8 | 0% | 41.07%
2024-11-28 09:00 | 11 | 28 | 9 | 3.846% | 39.77%
2024-11-28 10:00 | 11 | 28 | 10 | 8.714% | 38.11%
2024-11-28 11:00 | 11 | 28 | 11 | 11.27% | 37.22%
2024-11-28 12:00 | 11 | 28 | 12 | 8.929% | 36.22%
2024-11-28 13:00 | 11 | 28 | 13 | 7.858% | 35.82%
2024-11-28 14:00 | 11 | 28 | 14 | 3.977% | 36.29%
2024-11-28 15:00 | 11 | 28 | 15 | 0% | 37.75%
2024-11-28 16:00 | 11 | 28 | 16 | 0% | 39.12%
2024-11-28 17:00 | 11 | 28 | 17 | 0% | 39.58%
2024-11-28 18:00 | 11 | 28 | 18 | 0% | 39.88%
2024-11-28 19:00 | 11 | 28 | 19 | 0% | 39.99%
2024-11-28 20:00 | 11 | 28 | 20 | 0% | 39.77%
2024-11-28 21:00 | 11 | 28 | 21 | 0% | 39.7%
2024-11-28 22:00 | 11 | 28 | 22 | 0% | 39.82%
2024-11-28 23:00 | 11 | 28 | 23 | 0% | 40.16%
2024-11-29 | 11 | 29 | 0 | 0% | 34.61%
2024-11-29 01:00 | 11 | 29 | 1 | 0% | 39.95%
2024-11-29 02:00 | 11 | 29 | 2 | 0% | 40.48%
2024-11-29 03:00 | 11 | 29 | 3 | 0% | 41.02%
2024-11-29 04:00 | 11 | 29 | 4 | 0% | 42.01%
2024-11-29 05:00 | 11 | 29 | 5 | 0% | 42.76%
2024-11-29 06:00 | 11 | 29 | 6 | 0% | 41.83%
2024-11-29 07:00 | 11 | 29 | 7 | 0% | 43.65%
2024-11-29 08:00 | 11 | 29 | 8 | 0% | 43.99%
2024-11-29 09:00 | 11 | 29 | 9 | 0.5024% | 43.75%
2024-11-29 10:00 | 11 | 29 | 10 | 0.8496% | 43.44%
2024-11-29 11:00 | 11 | 29 | 11 | 1.117% | 43.1%
2024-11-29 12:00 | 11 | 29 | 12 | 0.4416% | 46.58%
2024-11-29 13:00 | 11 | 29 | 13 | 0.4267% | 41.17%
2024-11-29 14:00 | 11 | 29 | 14 | 0% | 42.44%
2024-11-29 15:00 | 11 | 29 | 15 | 0% | 42.98%
2024-11-29 16:00 | 11 | 29 | 16 | 0% | 42.94%
2024-11-29 17:00 | 11 | 29 | 17 | 0% | 50.52%
2024-11-29 18:00 | 11 | 29 | 18 | 0% | 40.67%
2024-11-29 19:00 | 11 | 29 | 19 | 0% | 39.74%
2024-11-29 20:00 | 11 | 29 | 20 | 0% | 38.09%
2024-11-29 21:00 | 11 | 29 | 21 | 0% | 37.17%
2024-11-29 22:00 | 11 | 29 | 22 | 0% | 36.59%
2024-11-29 23:00 | 11 | 29 | 23 | 0% | 35.34%
2024-11-30 | 11 | 30 | 0 | 0% | 41.77%
2024-11-30 01:00 | 11 | 30 | 1 | 0% | 34.32%
2024-11-30 02:00 | 11 | 30 | 2 | 0% | 34.36%
2024-11-30 03:00 | 11 | 30 | 3 | 0% | 34.66%
2024-11-30 04:00 | 11 | 30 | 4 | 0% | 35.07%
2024-11-30 05:00 | 11 | 30 | 5 | 0% | 36.01%
2024-11-30 06:00 | 11 | 30 | 6 | 0% | 36.98%
2024-11-30 07:00 | 11 | 30 | 7 | 0% | 41.46%
2024-11-30 08:00 | 11 | 30 | 8 | 0% | 38.89%
2024-11-30 09:00 | 11 | 30 | 9 | 2.293% | 39.78%
2024-11-30 10:00 | 11 | 30 | 10 | 4.252% | 40.11%
2024-11-30 11:00 | 11 | 30 | 11 | 8.731% | 39.8%
2024-11-30 12:00 | 11 | 30 | 12 | 11.64% | 39.53%
2024-11-30 13:00 | 11 | 30 | 13 | 13.95% | 39.39%
2024-11-30 14:00 | 11 | 30 | 14 | 5.279% | 39.96%
2024-11-30 15:00 | 11 | 30 | 15 | 0% | 40.32%
2024-11-30 16:00 | 11 | 30 | 16 | 0% | 40.81%
2024-11-30 17:00 | 11 | 30 | 17 | 0% | 41.08%
2024-11-30 18:00 | 11 | 30 | 18 | 0% | 41.79%
2024-11-30 19:00 | 11 | 30 | 19 | 0% | 43.53%
2024-11-30 20:00 | 11 | 30 | 20 | 0% | 42.01%
2024-11-30 21:00 | 11 | 30 | 21 | 0% | 42.21%
2024-11-30 22:00 | 11 | 30 | 22 | 0% | 42.52%
2024-11-30 23:00 | 11 | 30 | 23 | 0% | 42.25%
2024-12-01 | 12 | 1 | 0 | 0% | 48.75%
2024-12-01 01:00 | 12 | 1 | 1 | 0% | 41.12%
2024-12-01 02:00 | 12 | 1 | 2 | 0% | 40.37%
2024-12-01 03:00 | 12 | 1 | 3 | 0% | 39.8%
2024-12-01 04:00 | 12 | 1 | 4 | 0% | 39.14%
2024-12-01 05:00 | 12 | 1 | 5 | 0% | 38.59%
2024-12-01 06:00 | 12 | 1 | 6 | 0% | 37.7%
2024-12-01 07:00 | 12 | 1 | 7 | 0% | 36.76%
2024-12-01 08:00 | 12 | 1 | 8 | 0% | 38.43%
2024-12-01 09:00 | 12 | 1 | 9 | 3.911% | 38.01%
2024-12-01 10:00 | 12 | 1 | 10 | 6.8% | 34.48%
2024-12-01 11:00 | 12 | 1 | 11 | 10.12% | 33.05%
2024-12-01 12:00 | 12 | 1 | 12 | 10.11% | 32.28%
2024-12-01 13:00 | 12 | 1 | 13 | 6.55% | 31.91%
2024-12-01 14:00 | 12 | 1 | 14 | 3.496% | 32.59%
2024-12-01 15:00 | 12 | 1 | 15 | 0% | 33.66%
2024-12-01 16:00 | 12 | 1 | 16 | 0% | 34.71%
2024-12-01 17:00 | 12 | 1 | 17 | 0% | 35.29%
2024-12-01 18:00 | 12 | 1 | 18 | 0% | 35.9%
2024-12-01 19:00 | 12 | 1 | 19 | 0% | 35.89%
2024-12-01 20:00 | 12 | 1 | 20 | 0% | 35.81%
2024-12-01 21:00 | 12 | 1 | 21 | 0% | 35.64%
2024-12-01 22:00 | 12 | 1 | 22 | 0% | 35.85%
2024-12-01 23:00 | 12 | 1 | 23 | 0% | 35.97%
2024-12-02 | 12 | 2 | 0 | 0% | 40.46%
2024-12-02 01:00 | 12 | 2 | 1 | 0% | 49.81%
2024-12-02 02:00 | 12 | 2 | 2 | 0% | 50.39%
2024-12-02 03:00 | 12 | 2 | 3 | 0% | 52.99%
2024-12-02 04:00 | 12 | 2 | 4 | 0% | 51.91%
2024-12-02 05:00 | 12 | 2 | 5 | 0% | 52.89%
2024-12-02 06:00 | 12 | 2 | 6 | 0% | 53.61%
2024-12-02 07:00 | 12 | 2 | 7 | 0% | 53.22%
2024-12-02 08:00 | 12 | 2 | 8 | 0% | 52.49%
2024-12-02 09:00 | 12 | 2 | 9 | 4.374% | 52%
2024-12-02 10:00 | 12 | 2 | 10 | 9.895% | 51.14%
2024-12-02 11:00 | 12 | 2 | 11 | 12.48% | 51.42%
2024-12-02 12:00 | 12 | 2 | 12 | 19.4% | 48.49%
2024-12-02 13:00 | 12 | 2 | 13 | 7.683% | 47.92%
2024-12-02 14:00 | 12 | 2 | 14 | 2.933% | 47.96%
2024-12-02 15:00 | 12 | 2 | 15 | 0% | 48%
2024-12-02 16:00 | 12 | 2 | 16 | 0% | 48.51%
2024-12-02 17:00 | 12 | 2 | 17 | 0% | 48.31%
2024-12-02 18:00 | 12 | 2 | 18 | 0% | 47.73%
2024-12-02 19:00 | 12 | 2 | 19 | 0% | 46.96%
2024-12-02 20:00 | 12 | 2 | 20 | 0% | 46.23%
2024-12-02 21:00 | 12 | 2 | 21 | 0% | 44.4%
2024-12-02 22:00 | 12 | 2 | 22 | 0% | 42.62%
2024-12-02 23:00 | 12 | 2 | 23 | 0% | 40.75%
2024-12-03 | 12 | 3 | 0 | 0% | 26.15%
2024-12-03 01:00 | 12 | 3 | 1 | 0% | 38.87%
2024-12-03 02:00 | 12 | 3 | 2 | 0% | 37.04%
2024-12-03 03:00 | 12 | 3 | 3 | 0% | 35.39%
2024-12-03 04:00 | 12 | 3 | 4 | 0% | 33.86%
2024-12-03 05:00 | 12 | 3 | 5 | 0% | 32.91%
2024-12-03 06:00 | 12 | 3 | 6 | 0% | 31.66%
2024-12-03 07:00 | 12 | 3 | 7 | 0% | 30.73%
2024-12-03 08:00 | 12 | 3 | 8 | 0% | 28.47%
2024-12-03 09:00 | 12 | 3 | 9 | 0.5316% | 28.9%
2024-12-03 10:00 | 12 | 3 | 10 | 1.809% | 27.56%
2024-12-03 11:00 | 12 | 3 | 11 | 1.93% | 27.65%
2024-12-03 12:00 | 12 | 3 | 12 | 1.136% | 24.71%
2024-12-03 13:00 | 12 | 3 | 13 | 0.7287% | 24.03%
2024-12-03 14:00 | 12 | 3 | 14 | 0.4356% | 23.73%
2024-12-03 15:00 | 12 | 3 | 15 | 0% | 23.95%
2024-12-03 16:00 | 12 | 3 | 16 | 0% | 24.34%
2024-12-03 17:00 | 12 | 3 | 17 | 0% | 24.46%
2024-12-03 18:00 | 12 | 3 | 18 | 0% | 24.36%
2024-12-03 19:00 | 12 | 3 | 19 | 0% | 24.18%
2024-12-03 20:00 | 12 | 3 | 20 | 0% | 23.92%
2024-12-03 21:00 | 12 | 3 | 21 | 0% | 24.08%
2024-12-03 22:00 | 12 | 3 | 22 | 0% | 24.67%
2024-12-03 23:00 | 12 | 3 | 23 | 0% | 25.27%
2024-12-04 | 12 | 4 | 0 | 0% | 38.26%
2024-12-04 01:00 | 12 | 4 | 1 | 0% | 32.14%
2024-12-04 02:00 | 12 | 4 | 2 | 0% | 32.6%
2024-12-04 03:00 | 12 | 4 | 3 | 0% | 31.55%
2024-12-04 04:00 | 12 | 4 | 4 | 0% | 32.55%
2024-12-04 05:00 | 12 | 4 | 5 | 0% | 33.07%
2024-12-04 06:00 | 12 | 4 | 6 | 0% | 33.31%
2024-12-04 07:00 | 12 | 4 | 7 | 0% | 33.07%
2024-12-04 08:00 | 12 | 4 | 8 | 0% | 33.31%
2024-12-04 09:00 | 12 | 4 | 9 | 1.255% | 32.82%
2024-12-04 10:00 | 12 | 4 | 10 | 3.683% | 32.11%
2024-12-04 11:00 | 12 | 4 | 11 | 5.298% | 31.08%
2024-12-04 12:00 | 12 | 4 | 12 | 7.658% | 30.27%
2024-12-04 13:00 | 12 | 4 | 13 | 6.397% | 30.32%
2024-12-04 14:00 | 12 | 4 | 14 | 2.114% | 31.52%
2024-12-04 15:00 | 12 | 4 | 15 | 0% | 34.16%
2024-12-04 16:00 | 12 | 4 | 16 | 0% | 36.88%
2024-12-04 17:00 | 12 | 4 | 17 | 0% | 38.24%
2024-12-04 18:00 | 12 | 4 | 18 | 0% | 38.94%
2024-12-04 19:00 | 12 | 4 | 19 | 0% | 39.39%
2024-12-04 20:00 | 12 | 4 | 20 | 0% | 39.3%
2024-12-04 21:00 | 12 | 4 | 21 | 0% | 39.05%
2024-12-04 22:00 | 12 | 4 | 22 | 0% | 38.99%
2024-12-04 23:00 | 12 | 4 | 23 | 0% | 38.87%
2024-12-05 | 12 | 5 | 0 | 0% | 35.82%
2024-12-05 01:00 | 12 | 5 | 1 | 0% | 38.04%
2024-12-05 02:00 | 12 | 5 | 2 | 0% | 37.83%
2024-12-05 03:00 | 12 | 5 | 3 | 0% | 38.06%
2024-12-05 04:00 | 12 | 5 | 4 | 0% | 37.75%
2024-12-05 05:00 | 12 | 5 | 5 | 0% | 37.74%
2024-12-05 06:00 | 12 | 5 | 6 | 0% | 37.7%
2024-12-05 07:00 | 12 | 5 | 7 | 0% | 37.72%
2024-12-05 08:00 | 12 | 5 | 8 | 0% | 37.2%
2024-12-05 09:00 | 12 | 5 | 9 | 1.764% | 37.11%
2024-12-05 10:00 | 12 | 5 | 10 | 4.07% | 37%
2024-12-05 11:00 | 12 | 5 | 11 | 5.088% | 36.04%
2024-12-05 12:00 | 12 | 5 | 12 | 5.311% | 35.59%
2024-12-05 13:00 | 12 | 5 | 13 | 4.402% | 35.95%
2024-12-05 14:00 | 12 | 5 | 14 | 2.261% | 37.18%
2024-12-05 15:00 | 12 | 5 | 15 | 0% | 38.77%
2024-12-05 16:00 | 12 | 5 | 16 | 0% | 40.26%
2024-12-05 17:00 | 12 | 5 | 17 | 0% | 38.32%
2024-12-05 18:00 | 12 | 5 | 18 | 0% | 39.92%
2024-12-05 19:00 | 12 | 5 | 19 | 0% | 39.72%
2024-12-05 20:00 | 12 | 5 | 20 | 0% | 39.88%
2024-12-05 21:00 | 12 | 5 | 21 | 0% | 38.64%
2024-12-05 22:00 | 12 | 5 | 22 | 0% | 37.75%
2024-12-05 23:00 | 12 | 5 | 23 | 0% | 36.61%
2024-12-06 | 12 | 6 | 0 | 0% | 33.5%
2024-12-06 01:00 | 12 | 6 | 1 | 0% | 34.81%
2024-12-06 02:00 | 12 | 6 | 2 | 0% | 34.12%
2024-12-06 03:00 | 12 | 6 | 3 | 0% | 33.51%
2024-12-06 04:00 | 12 | 6 | 4 | 0% | 32.47%
2024-12-06 05:00 | 12 | 6 | 5 | 0% | 31.35%
2024-12-06 06:00 | 12 | 6 | 6 | 0% | 30.43%
2024-12-06 07:00 | 12 | 6 | 7 | 0% | 29.28%
2024-12-06 08:00 | 12 | 6 | 8 | 0% | 27.98%
2024-12-06 09:00 | 12 | 6 | 9 | 2.071% | 26.74%
2024-12-06 10:00 | 12 | 6 | 10 | 6.256% | 21.22%
2024-12-06 11:00 | 12 | 6 | 11 | 7.007% | 24.03%
2024-12-06 12:00 | 12 | 6 | 12 | 7.787% | 23.24%
2024-12-06 13:00 | 12 | 6 | 13 | 7.051% | 22.87%
2024-12-06 14:00 | 12 | 6 | 14 | 4.883% | 22.81%
2024-12-06 15:00 | 12 | 6 | 15 | 0% | 23.13%
2024-12-06 16:00 | 12 | 6 | 16 | 0% | 23.81%
2024-12-06 17:00 | 12 | 6 | 17 | 0% | 24.71%
2024-12-06 18:00 | 12 | 6 | 18 | 0% | 25.45%
2024-12-06 19:00 | 12 | 6 | 19 | 0% | 26.26%
2024-12-06 20:00 | 12 | 6 | 20 | 0% | 27.48%
2024-12-06 21:00 | 12 | 6 | 21 | 0% | 29.17%
2024-12-06 22:00 | 12 | 6 | 22 | 0% | 30.53%
2024-12-06 23:00 | 12 | 6 | 23 | 0% | 31.68%
2024-12-07 | 12 | 7 | 0 | 0% | 36.33%
2024-12-07 01:00 | 12 | 7 | 1 | 0% | 34.01%
2024-12-07 02:00 | 12 | 7 | 2 | 0% | 34.24%
2024-12-07 03:00 | 12 | 7 | 3 | 0% | 34.33%
2024-12-07 04:00 | 12 | 7 | 4 | 0% | 34.81%
2024-12-07 05:00 | 12 | 7 | 5 | 0% | 34.91%
2024-12-07 06:00 | 12 | 7 | 6 | 0% | 34.9%
2024-12-07 07:00 | 12 | 7 | 7 | 0% | 34.99%
2024-12-07 08:00 | 12 | 7 | 8 | 0% | 35.1%
2024-12-07 09:00 | 12 | 7 | 9 | 5.349% | 35.11%
2024-12-07 10:00 | 12 | 7 | 10 | 9.831% | 34.89%
2024-12-07 11:00 | 12 | 7 | 11 | 13.2% | 35.37%
2024-12-07 12:00 | 12 | 7 | 12 | 6.181% | 34.76%
2024-12-07 13:00 | 12 | 7 | 13 | 6.84% | 34.51%
2024-12-07 14:00 | 12 | 7 | 14 | 2.178% | 34.9%
2024-12-07 15:00 | 12 | 7 | 15 | 0% | 35.68%
2024-12-07 16:00 | 12 | 7 | 16 | 0% | 36.85%
2024-12-07 17:00 | 12 | 7 | 17 | 0% | 37.58%
2024-12-07 18:00 | 12 | 7 | 18 | 0% | 37.99%
2024-12-07 19:00 | 12 | 7 | 19 | 0% | 37.29%
2024-12-07 20:00 | 12 | 7 | 20 | 0% | 36.58%
2024-12-07 21:00 | 12 | 7 | 21 | 0% | 36.24%
2024-12-07 22:00 | 12 | 7 | 22 | 0% | 35.99%
2024-12-07 23:00 | 12 | 7 | 23 | 0% | 35.9%
2024-12-08 | 12 | 8 | 0 | 0% | 44.04%
2024-12-08 01:00 | 12 | 8 | 1 | 0% | 36.42%
2024-12-08 02:00 | 12 | 8 | 2 | 0% | 36.34%
2024-12-08 03:00 | 12 | 8 | 3 | 0% | 36.05%
2024-12-08 04:00 | 12 | 8 | 4 | 0% | 32.65%
2024-12-08 05:00 | 12 | 8 | 5 | 0% | 36.43%
2024-12-08 06:00 | 12 | 8 | 6 | 0% | 36.88%
2024-12-08 07:00 | 12 | 8 | 7 | 0% | 37.46%
2024-12-08 08:00 | 12 | 8 | 8 | 0% | 37.59%
2024-12-08 09:00 | 12 | 8 | 9 | 5.184% | 38.4%
2024-12-08 10:00 | 12 | 8 | 10 | 9.424% | 38.96%
2024-12-08 11:00 | 12 | 8 | 11 | 8.766% | 38.84%
2024-12-08 12:00 | 12 | 8 | 12 | 8.334% | 39%
2024-12-08 13:00 | 12 | 8 | 13 | 8.213% | 39.59%
2024-12-08 14:00 | 12 | 8 | 14 | 4.797% | 40.5%
2024-12-08 15:00 | 12 | 8 | 15 | 0% | 42.04%
2024-12-08 16:00 | 12 | 8 | 16 | 0% | 43.63%
2024-12-08 17:00 | 12 | 8 | 17 | 0% | 44.74%
2024-12-08 18:00 | 12 | 8 | 18 | 0% | 45.12%
2024-12-08 19:00 | 12 | 8 | 19 | 0% | 45.05%
2024-12-08 20:00 | 12 | 8 | 20 | 0% | 44.63%
2024-12-08 21:00 | 12 | 8 | 21 | 0% | 44.31%
2024-12-08 22:00 | 12 | 8 | 22 | 0% | 44.22%
2024-12-08 23:00 | 12 | 8 | 23 | 0% | 44.13%
2024-12-09 | 12 | 9 | 0 | 0% | 32.41%
2024-12-09 01:00 | 12 | 9 | 1 | 0% | 43.09%
2024-12-09 02:00 | 12 | 9 | 2 | 0% | 42.27%
2024-12-09 03:00 | 12 | 9 | 3 | 0% | 42.09%
2024-12-09 04:00 | 12 | 9 | 4 | 0% | 41.63%
2024-12-09 05:00 | 12 | 9 | 5 | 0% | 41.38%
2024-12-09 06:00 | 12 | 9 | 6 | 0% | 43.73%
2024-12-09 07:00 | 12 | 9 | 7 | 0% | 39.98%
2024-12-09 08:00 | 12 | 9 | 8 | 0% | 38.66%
2024-12-09 09:00 | 12 | 9 | 9 | 0.3149% | 37.54%
2024-12-09 10:00 | 12 | 9 | 10 | 0.7231% | 36.15%
2024-12-09 11:00 | 12 | 9 | 11 | 1.295% | 34.07%
2024-12-09 12:00 | 12 | 9 | 12 | 0.7145% | 31.9%
2024-12-09 13:00 | 12 | 9 | 13 | 0.553% | 31.07%
2024-12-09 14:00 | 12 | 9 | 14 | 0.2816% | 30.5%
2024-12-09 15:00 | 12 | 9 | 15 | 0% | 31.38%
2024-12-09 16:00 | 12 | 9 | 16 | 0% | 32.1%
2024-12-09 17:00 | 12 | 9 | 17 | 0% | 32.52%
2024-12-09 18:00 | 12 | 9 | 18 | 0% | 32.71%
2024-12-09 19:00 | 12 | 9 | 19 | 0% | 33.06%
2024-12-09 20:00 | 12 | 9 | 20 | 0% | 33.58%
2024-12-09 21:00 | 12 | 9 | 21 | 0% | 34.05%
2024-12-09 22:00 | 12 | 9 | 22 | 0% | 33.96%
2024-12-09 23:00 | 12 | 9 | 23 | 0% | 33.24%
2024-12-10 | 12 | 10 | 0 | 0% | 35.1%
2024-12-10 01:00 | 12 | 10 | 1 | 0% | 31.78%
2024-12-10 02:00 | 12 | 10 | 2 | 0% | 31.36%
2024-12-10 03:00 | 12 | 10 | 3 | 0% | 30.98%
2024-12-10 04:00 | 12 | 10 | 4 | 0% | 30.29%
2024-12-10 05:00 | 12 | 10 | 5 | 0% | 29.72%
2024-12-10 06:00 | 12 | 10 | 6 | 0% | 29.39%
2024-12-10 07:00 | 12 | 10 | 7 | 0% | 28.97%
2024-12-10 08:00 | 12 | 10 | 8 | 0% | 28.8%
2024-12-10 09:00 | 12 | 10 | 9 | 1.988% | 28.18%
2024-12-10 10:00 | 12 | 10 | 10 | 6.033% | 27.08%
2024-12-10 11:00 | 12 | 10 | 11 | 9.11% | 26.41%
2024-12-10 12:00 | 12 | 10 | 12 | 7.459% | 22.55%
2024-12-10 13:00 | 12 | 10 | 13 | 5.69% | 26.71%
2024-12-10 14:00 | 12 | 10 | 14 | 3.32% | 28.42%
2024-12-10 15:00 | 12 | 10 | 15 | 0% | 30.5%
2024-12-10 16:00 | 12 | 10 | 16 | 0% | 32.02%
2024-12-10 17:00 | 12 | 10 | 17 | 0% | 33.29%
2024-12-10 18:00 | 12 | 10 | 18 | 0% | 34.51%
2024-12-10 19:00 | 12 | 10 | 19 | 0% | 35.19%
2024-12-10 20:00 | 12 | 10 | 20 | 0% | 35.46%
2024-12-10 21:00 | 12 | 10 | 21 | 0% | 35.73%
2024-12-10 22:00 | 12 | 10 | 22 | 0% | 35.44%
2024-12-10 23:00 | 12 | 10 | 23 | 0% | 35.17%
2024-12-11 | 12 | 11 | 0 | 0% | 22.54%
2024-12-11 01:00 | 12 | 11 | 1 | 0% | 34.94%
2024-12-11 02:00 | 12 | 11 | 2 | 0% | 34.31%
2024-12-11 03:00 | 12 | 11 | 3 | 0% | 33.77%
2024-12-11 04:00 | 12 | 11 | 4 | 0% | 33.28%
2024-12-11 05:00 | 12 | 11 | 5 | 0% | 32.97%
2024-12-11 06:00 | 12 | 11 | 6 | 0% | 27.74%
2024-12-11 07:00 | 12 | 11 | 7 | 0% | 36.23%
2024-12-11 08:00 | 12 | 11 | 8 | 0% | 32.75%
2024-12-11 09:00 | 12 | 11 | 9 | 2.018% | 31.69%
2024-12-11 10:00 | 12 | 11 | 10 | 6.525% | 30.63%
2024-12-11 11:00 | 12 | 11 | 11 | 9.174% | 28.99%
2024-12-11 12:00 | 12 | 11 | 12 | 9.316% | 27.32%
2024-12-11 13:00 | 12 | 11 | 13 | 6.965% | 26.46%
2024-12-11 14:00 | 12 | 11 | 14 | 3.936% | 26.22%
2024-12-11 15:00 | 12 | 11 | 15 | 0% | 26.97%
2024-12-11 16:00 | 12 | 11 | 16 | 0% | 27.27%
2024-12-11 17:00 | 12 | 11 | 17 | 0% | 27.52%
2024-12-11 18:00 | 12 | 11 | 18 | 0% | 27.45%
2024-12-11 19:00 | 12 | 11 | 19 | 0% | 30%
2024-12-11 20:00 | 12 | 11 | 20 | 0% | 26.84%
2024-12-11 21:00 | 12 | 11 | 21 | 0% | 25.61%
2024-12-11 22:00 | 12 | 11 | 22 | 0% | 24.41%
2024-12-11 23:00 | 12 | 11 | 23 | 0% | 23.46%
2024-12-12 | 12 | 12 | 0 | 0% | 24.07%
2024-12-12 01:00 | 12 | 12 | 1 | 0% | 22.78%
2024-12-12 02:00 | 12 | 12 | 2 | 0% | 22.51%
2024-12-12 03:00 | 12 | 12 | 3 | 0% | 22.13%
2024-12-12 04:00 | 12 | 12 | 4 | 0% | 22.19%
2024-12-12 05:00 | 12 | 12 | 5 | 0% | 22.24%
2024-12-12 06:00 | 12 | 12 | 6 | 0% | 22.58%
2024-12-12 07:00 | 12 | 12 | 7 | 0% | 22.56%
2024-12-12 08:00 | 12 | 12 | 8 | 0% | 22.88%
2024-12-12 09:00 | 12 | 12 | 9 | 4.862% | 23.06%
2024-12-12 10:00 | 12 | 12 | 10 | 13.6% | 22.5%
2024-12-12 11:00 | 12 | 12 | 11 | 16.88% | 21.88%
2024-12-12 12:00 | 12 | 12 | 12 | 15.77% | 21.16%
2024-12-12 13:00 | 12 | 12 | 13 | 10.5% | 21.32%
2024-12-12 14:00 | 12 | 12 | 14 | 2.556% | 21.93%
2024-12-12 15:00 | 12 | 12 | 15 | 0% | 23.13%
2024-12-12 16:00 | 12 | 12 | 16 | 0% | 23.52%
2024-12-12 17:00 | 12 | 12 | 17 | 0% | 23.27%
2024-12-12 18:00 | 12 | 12 | 18 | 0% | 23.1%
2024-12-12 19:00 | 12 | 12 | 19 | 0% | 23.31%
2024-12-12 20:00 | 12 | 12 | 20 | 0% | 22.88%
2024-12-12 21:00 | 12 | 12 | 21 | 0% | 22.58%
2024-12-12 22:00 | 12 | 12 | 22 | 0% | 22.75%
2024-12-12 23:00 | 12 | 12 | 23 | 0% | 23.18%
2024-12-13 | 12 | 13 | 0 | 0% | 33.54%
2024-12-13 01:00 | 12 | 13 | 1 | 0% | 24.77%
2024-12-13 02:00 | 12 | 13 | 2 | 0% | 25.45%
2024-12-13 03:00 | 12 | 13 | 3 | 0% | 26.31%
2024-12-13 04:00 | 12 | 13 | 4 | 0% | 27.14%
2024-12-13 05:00 | 12 | 13 | 5 | 0% | 27.88%
2024-12-13 06:00 | 12 | 13 | 6 | 0% | 28.61%
2024-12-13 07:00 | 12 | 13 | 7 | 0% | 29.13%
2024-12-13 08:00 | 12 | 13 | 8 | 0% | 29.54%
2024-12-13 09:00 | 12 | 13 | 9 | 4.718% | 30.38%
2024-12-13 10:00 | 12 | 13 | 10 | 8.735% | 30.42%
2024-12-13 11:00 | 12 | 13 | 11 | 17.35% | 30.07%
2024-12-13 12:00 | 12 | 13 | 12 | 14.61% | 30.05%
2024-12-13 13:00 | 12 | 13 | 13 | 12.96% | 33.09%
2024-12-13 14:00 | 12 | 13 | 14 | 4.938% | 31.63%
2024-12-13 15:00 | 12 | 13 | 15 | 0% | 32.75%
2024-12-13 16:00 | 12 | 13 | 16 | 0% | 31.07%
2024-12-13 17:00 | 12 | 13 | 17 | 0% | 33.79%
2024-12-13 18:00 | 12 | 13 | 18 | 0% | 34.01%
2024-12-13 19:00 | 12 | 13 | 19 | 0% | 34.87%
2024-12-13 20:00 | 12 | 13 | 20 | 0% | 34.49%
2024-12-13 21:00 | 12 | 13 | 21 | 0% | 34.22%
2024-12-13 22:00 | 12 | 13 | 22 | 0% | 33.75%
2024-12-13 23:00 | 12 | 13 | 23 | 0% | 33.4%
2024-12-14 | 12 | 14 | 0 | 0% | 31.74%
2024-12-14 01:00 | 12 | 14 | 1 | 0% | 33.24%
2024-12-14 02:00 | 12 | 14 | 2 | 0% | 32.85%
2024-12-14 03:00 | 12 | 14 | 3 | 0% | 31.99%
2024-12-14 04:00 | 12 | 14 | 4 | 0% | 31.27%
2024-12-14 05:00 | 12 | 14 | 5 | 0% | 30.47%
2024-12-14 06:00 | 12 | 14 | 6 | 0% | 29.88%
2024-12-14 07:00 | 12 | 14 | 7 | 0% | 29.46%
2024-12-14 08:00 | 12 | 14 | 8 | 0% | 28.84%
2024-12-14 09:00 | 12 | 14 | 9 | 3.985% | 28.23%
2024-12-14 10:00 | 12 | 14 | 10 | 8.495% | 27.16%
2024-12-14 11:00 | 12 | 14 | 11 | 11.16% | 25.5%
2024-12-14 12:00 | 12 | 14 | 12 | 8.776% | 24.21%
2024-12-14 13:00 | 12 | 14 | 13 | 5.203% | 23.73%
2024-12-14 14:00 | 12 | 14 | 14 | 2.677% | 24.06%
2024-12-14 15:00 | 12 | 14 | 15 | 0% | 25.95%
2024-12-14 16:00 | 12 | 14 | 16 | 0% | 25.88%
2024-12-14 17:00 | 12 | 14 | 17 | 0% | 26.56%
2024-12-14 18:00 | 12 | 14 | 18 | 0% | 26.97%
2024-12-14 19:00 | 12 | 14 | 19 | 0% | 27.25%
2024-12-14 20:00 | 12 | 14 | 20 | 0% | 30.92%
2024-12-14 21:00 | 12 | 14 | 21 | 0% | 29.48%
2024-12-14 22:00 | 12 | 14 | 22 | 0% | 30.35%
2024-12-14 23:00 | 12 | 14 | 23 | 0% | 31.04%
2024-12-15 | 12 | 15 | 0 | 0% | 39.88%
2024-12-15 01:00 | 12 | 15 | 1 | 0% | 31.84%
2024-12-15 02:00 | 12 | 15 | 2 | 0% | 31.74%
2024-12-15 03:00 | 12 | 15 | 3 | 0% | 31.25%
2024-12-15 04:00 | 12 | 15 | 4 | 0% | 30.97%
2024-12-15 05:00 | 12 | 15 | 5 | 0% | 30.61%
2024-12-15 06:00 | 12 | 15 | 6 | 0% | 29.54%
2024-12-15 07:00 | 12 | 15 | 7 | 0% | 28.51%
2024-12-15 08:00 | 12 | 15 | 8 | 0% | 27.66%
2024-12-15 09:00 | 12 | 15 | 9 | 0% | 27.18%
2024-12-15 10:00 | 12 | 15 | 10 | 0.618% | 27.49%
2024-12-15 11:00 | 12 | 15 | 11 | 0.7752% | 27.5%
2024-12-15 12:00 | 12 | 15 | 12 | 1.268% | 28.3%
2024-12-15 13:00 | 12 | 15 | 13 | 0% | 29.57%
2024-12-15 14:00 | 12 | 15 | 14 | 0.2017% | 30.67%
2024-12-15 15:00 | 12 | 15 | 15 | 0% | 31.89%
2024-12-15 16:00 | 12 | 15 | 16 | 0% | 33.33%
2024-12-15 17:00 | 12 | 15 | 17 | 0% | 34.63%
2024-12-15 18:00 | 12 | 15 | 18 | 0% | 35.87%
2024-12-15 19:00 | 12 | 15 | 19 | 0% | 37.06%
2024-12-15 20:00 | 12 | 15 | 20 | 0% | 38%
2024-12-15 21:00 | 12 | 15 | 21 | 0% | 38.58%
2024-12-15 22:00 | 12 | 15 | 22 | 0% | 39.27%
2024-12-15 23:00 | 12 | 15 | 23 | 0% | 41.83%
2024-12-16 | 12 | 16 | 0 | 0% | 42.68%
2024-12-16 01:00 | 12 | 16 | 1 | 0% | 40.46%
2024-12-16 02:00 | 12 | 16 | 2 | 0% | 40.63%
2024-12-16 03:00 | 12 | 16 | 3 | 0% | 41.91%
2024-12-16 04:00 | 12 | 16 | 4 | 0% | 42.52%
2024-12-16 05:00 | 12 | 16 | 5 | 0% | 43.38%
2024-12-16 06:00 | 12 | 16 | 6 | 0% | 43.85%
2024-12-16 07:00 | 12 | 16 | 7 | 0% | 44.24%
2024-12-16 08:00 | 12 | 16 | 8 | 0% | 44.17%
2024-12-16 09:00 | 12 | 16 | 9 | 0.2511% | 44.53%
2024-12-16 10:00 | 12 | 16 | 10 | 1.133% | 44.21%
2024-12-16 11:00 | 12 | 16 | 11 | 1.802% | 43.96%
2024-12-16 12:00 | 12 | 16 | 12 | 0.6112% | 43.75%
2024-12-16 13:00 | 12 | 16 | 13 | 0.4555% | 44.08%
2024-12-16 14:00 | 12 | 16 | 14 | 0% | 44.55%
2024-12-16 15:00 | 12 | 16 | 15 | 0% | 45.16%
2024-12-16 16:00 | 12 | 16 | 16 | 0% | 45.81%
2024-12-16 17:00 | 12 | 16 | 17 | 0% | 46.37%
2024-12-16 18:00 | 12 | 16 | 18 | 0% | 46.41%
2024-12-16 19:00 | 12 | 16 | 19 | 0% | 46.21%
2024-12-16 20:00 | 12 | 16 | 20 | 0% | 49.42%
2024-12-16 21:00 | 12 | 16 | 21 | 0% | 45.64%
2024-12-16 22:00 | 12 | 16 | 22 | 0% | 47.78%
2024-12-16 23:00 | 12 | 16 | 23 | 0% | 43.79%
2024-12-17 | 12 | 17 | 0 | 0% | 41.72%
2024-12-17 01:00 | 12 | 17 | 1 | 0% | 41.87%
2024-12-17 02:00 | 12 | 17 | 2 | 0% | 40.88%
2024-12-17 03:00 | 12 | 17 | 3 | 0% | 39.91%
2024-12-17 04:00 | 12 | 17 | 4 | 0% | 39.06%
2024-12-17 05:00 | 12 | 17 | 5 | 0% | 38.5%
2024-12-17 06:00 | 12 | 17 | 6 | 0% | 38.39%
2024-12-17 07:00 | 12 | 17 | 7 | 0% | 37.8%
2024-12-17 08:00 | 12 | 17 | 8 | 0% | 37.96%
2024-12-17 09:00 | 12 | 17 | 9 | 0% | 38.18%
2024-12-17 10:00 | 12 | 17 | 10 | 0% | 38.03%
2024-12-17 11:00 | 12 | 17 | 11 | 0.2467% | 37.53%
2024-12-17 12:00 | 12 | 17 | 12 | 1.892% | 37.13%
2024-12-17 13:00 | 12 | 17 | 13 | 0.7743% | 36.74%
2024-12-17 14:00 | 12 | 17 | 14 | 0% | 36.63%
2024-12-17 15:00 | 12 | 17 | 15 | 0% | 37.05%
2024-12-17 16:00 | 12 | 17 | 16 | 0% | 37.16%
2024-12-17 17:00 | 12 | 17 | 17 | 0% | 37.64%
2024-12-17 18:00 | 12 | 17 | 18 | 0% | 38.54%
2024-12-17 19:00 | 12 | 17 | 19 | 0% | 38.96%
2024-12-17 20:00 | 12 | 17 | 20 | 0% | 39.28%
2024-12-17 21:00 | 12 | 17 | 21 | 0% | 39.63%
2024-12-17 22:00 | 12 | 17 | 22 | 0% | 40.08%
2024-12-17 23:00 | 12 | 17 | 23 | 0% | 40.61%
2024-12-18 | 12 | 18 | 0 | 0% | 53.34%
2024-12-18 01:00 | 12 | 18 | 1 | 0% | 42.19%
2024-12-18 02:00 | 12 | 18 | 2 | 0% | 42.59%
2024-12-18 03:00 | 12 | 18 | 3 | 0% | 43.26%
2024-12-18 04:00 | 12 | 18 | 4 | 0% | 43.52%
2024-12-18 05:00 | 12 | 18 | 5 | 0% | 44.45%
2024-12-18 06:00 | 12 | 18 | 6 | 0% | 45.52%
2024-12-18 07:00 | 12 | 18 | 7 | 0% | 46.33%
2024-12-18 08:00 | 12 | 18 | 8 | 0% | 46.71%
2024-12-18 09:00 | 12 | 18 | 9 | 0.2633% | 46.9%
2024-12-18 10:00 | 12 | 18 | 10 | 2.419% | 46.96%
2024-12-18 11:00 | 12 | 18 | 11 | 3.162% | 46.95%
2024-12-18 12:00 | 12 | 18 | 12 | 3.248% | 47.62%
2024-12-18 13:00 | 12 | 18 | 13 | 2.667% | 48.26%
2024-12-18 14:00 | 12 | 18 | 14 | 0.8418% | 49.12%
2024-12-18 15:00 | 12 | 18 | 15 | 0% | 50.24%
2024-12-18 16:00 | 12 | 18 | 16 | 0% | 50.88%
2024-12-18 17:00 | 12 | 18 | 17 | 0% | 50.75%
2024-12-18 18:00 | 12 | 18 | 18 | 0% | 51.14%
2024-12-18 19:00 | 12 | 18 | 19 | 0% | 51.85%
2024-12-18 20:00 | 12 | 18 | 20 | 0% | 51.69%
2024-12-18 21:00 | 12 | 18 | 21 | 0% | 52.3%
2024-12-18 22:00 | 12 | 18 | 22 | 0% | 52.7%
2024-12-18 23:00 | 12 | 18 | 23 | 0% | 53.38%
2024-12-19 | 12 | 19 | 0 | 0% | 45.28%
2024-12-19 01:00 | 12 | 19 | 1 | 0% | 53.44%
2024-12-19 02:00 | 12 | 19 | 2 | 0% | 53.23%
2024-12-19 03:00 | 12 | 19 | 3 | 0% | 52.81%
2024-12-19 04:00 | 12 | 19 | 4 | 0% | 52.14%
2024-12-19 05:00 | 12 | 19 | 5 | 0% | 51.26%
2024-12-19 06:00 | 12 | 19 | 6 | 0% | 50.2%
2024-12-19 07:00 | 12 | 19 | 7 | 0% | 49.26%
2024-12-19 08:00 | 12 | 19 | 8 | 0% | 47.83%
2024-12-19 09:00 | 12 | 19 | 9 | 2.425% | 46.61%
2024-12-19 10:00 | 12 | 19 | 10 | 7.534% | 44.77%
2024-12-19 11:00 | 12 | 19 | 11 | 6.475% | 43.17%
2024-12-19 12:00 | 12 | 19 | 12 | 3.722% | 42.04%
2024-12-19 13:00 | 12 | 19 | 13 | 3.284% | 41.75%
2024-12-19 14:00 | 12 | 19 | 14 | 1.061% | 42.57%
2024-12-19 15:00 | 12 | 19 | 15 | 0% | 44.7%
2024-12-19 16:00 | 12 | 19 | 16 | 0% | 46.99%
2024-12-19 17:00 | 12 | 19 | 17 | 0% | 49.02%
2024-12-19 18:00 | 12 | 19 | 18 | 0% | 49.92%
2024-12-19 19:00 | 12 | 19 | 19 | 0% | 49.85%
2024-12-19 20:00 | 12 | 19 | 20 | 0% | 49.61%
2024-12-19 21:00 | 12 | 19 | 21 | 0% | 48.29%
2024-12-19 22:00 | 12 | 19 | 22 | 0% | 47.26%
2024-12-19 23:00 | 12 | 19 | 23 | 0% | 46.5%
2024-12-20 | 12 | 20 | 0 | 0% | 35.88%
2024-12-20 01:00 | 12 | 20 | 1 | 0% | 45.22%
2024-12-20 02:00 | 12 | 20 | 2 | 0% | 45.78%
2024-12-20 03:00 | 12 | 20 | 3 | 0% | 46.02%
2024-12-20 04:00 | 12 | 20 | 4 | 0% | 45.41%
2024-12-20 05:00 | 12 | 20 | 5 | 0% | 45.29%
2024-12-20 06:00 | 12 | 20 | 6 | 0% | 45.05%
2024-12-20 07:00 | 12 | 20 | 7 | 0% | 44.45%
2024-12-20 08:00 | 12 | 20 | 8 | 0% | 43.58%
2024-12-20 09:00 | 12 | 20 | 9 | 0.55% | 42.94%
2024-12-20 10:00 | 12 | 20 | 10 | 3.066% | 42.14%
2024-12-20 11:00 | 12 | 20 | 11 | 4.805% | 41.55%
2024-12-20 12:00 | 12 | 20 | 12 | 5.476% | 41.07%
2024-12-20 13:00 | 12 | 20 | 13 | 3.403% | 40.55%
2024-12-20 14:00 | 12 | 20 | 14 | 1.057% | 40.37%
2024-12-20 15:00 | 12 | 20 | 15 | 0% | 40.52%
2024-12-20 16:00 | 12 | 20 | 16 | 0% | 40.88%
2024-12-20 17:00 | 12 | 20 | 17 | 0% | 40.58%
2024-12-20 18:00 | 12 | 20 | 18 | 0% | 39.08%
2024-12-20 19:00 | 12 | 20 | 19 | 0% | 37.56%
2024-12-20 20:00 | 12 | 20 | 20 | 0% | 36.87%
2024-12-20 21:00 | 12 | 20 | 21 | 0% | 36.74%
2024-12-20 22:00 | 12 | 20 | 22 | 0% | 35.79%
2024-12-20 23:00 | 12 | 20 | 23 | 0% | 35.29%
2024-12-21 | 12 | 21 | 0 | 0% | 44.35%
2024-12-21 01:00 | 12 | 21 | 1 | 0% | 35.47%
2024-12-21 02:00 | 12 | 21 | 2 | 0% | 35%
2024-12-21 03:00 | 12 | 21 | 3 | 0% | 34.78%
2024-12-21 04:00 | 12 | 21 | 4 | 0% | 34.86%
2024-12-21 05:00 | 12 | 21 | 5 | 0% | 35.21%
2024-12-21 06:00 | 12 | 21 | 6 | 0% | 35.95%
2024-12-21 07:00 | 12 | 21 | 7 | 0% | 36.87%
2024-12-21 08:00 | 12 | 21 | 8 | 0% | 37.98%
2024-12-21 09:00 | 12 | 21 | 9 | 3.24% | 39.87%
2024-12-21 10:00 | 12 | 21 | 10 | 9.898% | 40.78%
2024-12-21 11:00 | 12 | 21 | 11 | 15% | 41.41%
2024-12-21 12:00 | 12 | 21 | 12 | 15.92% | 41.96%
2024-12-21 13:00 | 12 | 21 | 13 | 10.12% | 41.57%
2024-12-21 14:00 | 12 | 21 | 14 | 2.137% | 41.39%
2024-12-21 15:00 | 12 | 21 | 15 | 0% | 41.56%
2024-12-21 16:00 | 12 | 21 | 16 | 0% | 42.13%
2024-12-21 17:00 | 12 | 21 | 17 | 0% | 42.86%
2024-12-21 18:00 | 12 | 21 | 18 | 0% | 43.83%
2024-12-21 19:00 | 12 | 21 | 19 | 0% | 44.58%
2024-12-21 20:00 | 12 | 21 | 20 | 0% | 45.59%
2024-12-21 21:00 | 12 | 21 | 21 | 0% | 45.6%
2024-12-21 22:00 | 12 | 21 | 22 | 0% | 44.94%
2024-12-21 23:00 | 12 | 21 | 23 | 0% | 44.55%
2024-12-22 | 12 | 22 | 0 | 0% | 41.83%
2024-12-22 01:00 | 12 | 22 | 1 | 0% | 43.91%
2024-12-22 02:00 | 12 | 22 | 2 | 0% | 43.66%
2024-12-22 03:00 | 12 | 22 | 3 | 0% | 44.14%
2024-12-22 04:00 | 12 | 22 | 4 | 0% | 45.6%
2024-12-22 05:00 | 12 | 22 | 5 | 0% | 45.79%
2024-12-22 06:00 | 12 | 22 | 6 | 0% | 45.9%
2024-12-22 07:00 | 12 | 22 | 7 | 0% | 45.8%
2024-12-22 08:00 | 12 | 22 | 8 | 0% | 45.01%
2024-12-22 09:00 | 12 | 22 | 9 | 2.553% | 44.13%
2024-12-22 10:00 | 12 | 22 | 10 | 7.544% | 42.43%
2024-12-22 11:00 | 12 | 22 | 11 | 7.946% | 40.95%
2024-12-22 12:00 | 12 | 22 | 12 | 2.948% | 39.67%
2024-12-22 13:00 | 12 | 22 | 13 | 4.325% | 38.24%
2024-12-22 14:00 | 12 | 22 | 14 | 2.974% | 37.21%
2024-12-22 15:00 | 12 | 22 | 15 | 0% | 37.36%
2024-12-22 16:00 | 12 | 22 | 16 | 0% | 37.34%
2024-12-22 17:00 | 12 | 22 | 17 | 0% | 37.76%
2024-12-22 18:00 | 12 | 22 | 18 | 0% | 41.29%
2024-12-22 19:00 | 12 | 22 | 19 | 0% | 38.51%
2024-12-22 20:00 | 12 | 22 | 20 | 0% | 38.92%
2024-12-22 21:00 | 12 | 22 | 21 | 0% | 39.81%
2024-12-22 22:00 | 12 | 22 | 22 | 0% | 39.98%
2024-12-22 23:00 | 12 | 22 | 23 | 0% | 44.24%
2024-12-23 | 12 | 23 | 0 | 0% | 34.47%
2024-12-23 01:00 | 12 | 23 | 1 | 0% | 41.3%
2024-12-23 02:00 | 12 | 23 | 2 | 0% | 40.51%
2024-12-23 03:00 | 12 | 23 | 3 | 0% | 39.62%
2024-12-23 04:00 | 12 | 23 | 4 | 0% | 38.98%
2024-12-23 05:00 | 12 | 23 | 5 | 0% | 38.48%
2024-12-23 06:00 | 12 | 23 | 6 | 0% | 37.97%
2024-12-23 07:00 | 12 | 23 | 7 | 0% | 41.02%
2024-12-23 08:00 | 12 | 23 | 8 | 0% | 36.99%
2024-12-23 09:00 | 12 | 23 | 9 | 0% | 36.97%
2024-12-23 10:00 | 12 | 23 | 10 | 0.3888% | 36.4%
2024-12-23 11:00 | 12 | 23 | 11 | 0.6263% | 35.63%
2024-12-23 12:00 | 12 | 23 | 12 | 0.3296% | 34.86%
2024-12-23 13:00 | 12 | 23 | 13 | 0.7924% | 34.77%
2024-12-23 14:00 | 12 | 23 | 14 | 0.5505% | 35.14%
2024-12-23 15:00 | 12 | 23 | 15 | 0% | 35.14%
2024-12-23 16:00 | 12 | 23 | 16 | 0% | 34.97%
2024-12-23 17:00 | 12 | 23 | 17 | 0% | 34.67%
2024-12-23 18:00 | 12 | 23 | 18 | 0% | 34.31%
2024-12-23 19:00 | 12 | 23 | 19 | 0% | 34.07%
2024-12-23 20:00 | 12 | 23 | 20 | 0% | 36.74%
2024-12-23 21:00 | 12 | 23 | 21 | 0% | 33.26%
2024-12-23 22:00 | 12 | 23 | 22 | 0% | 32.61%
2024-12-23 23:00 | 12 | 23 | 23 | 0% | 32.54%
2024-12-24 | 12 | 24 | 0 | 0% | 41.91%
2024-12-24 01:00 | 12 | 24 | 1 | 0% | 31.72%
2024-12-24 02:00 | 12 | 24 | 2 | 0% | 31.2%
2024-12-24 03:00 | 12 | 24 | 3 | 0% | 31.22%
2024-12-24 04:00 | 12 | 24 | 4 | 0% | 31.64%
2024-12-24 05:00 | 12 | 24 | 5 | 0% | 31.76%
2024-12-24 06:00 | 12 | 24 | 6 | 0% | 32.23%
2024-12-24 07:00 | 12 | 24 | 7 | 0% | 32.58%
2024-12-24 08:00 | 12 | 24 | 8 | 0% | 33.13%
2024-12-24 09:00 | 12 | 24 | 9 | 1.485% | 33.56%
2024-12-24 10:00 | 12 | 24 | 10 | 1.999% | 34.01%
2024-12-24 11:00 | 12 | 24 | 11 | 2.21% | 34.27%
2024-12-24 12:00 | 12 | 24 | 12 | 11.48% | 35.37%
2024-12-24 13:00 | 12 | 24 | 13 | 1.914% | 36.87%
2024-12-24 14:00 | 12 | 24 | 14 | 1.744% | 38.33%
2024-12-24 15:00 | 12 | 24 | 15 | 0% | 39.89%
2024-12-24 16:00 | 12 | 24 | 16 | 0% | 40.46%
2024-12-24 17:00 | 12 | 24 | 17 | 0% | 40.98%
2024-12-24 18:00 | 12 | 24 | 18 | 0% | 45.43%
2024-12-24 19:00 | 12 | 24 | 19 | 0% | 41.26%
2024-12-24 20:00 | 12 | 24 | 20 | 0% | 40.75%
2024-12-24 21:00 | 12 | 24 | 21 | 0% | 40.92%
2024-12-24 22:00 | 12 | 24 | 22 | 0% | 40.96%
2024-12-24 23:00 | 12 | 24 | 23 | 0% | 41.1%
2024-12-25 | 12 | 25 | 0 | 0% | 46.58%
2024-12-25 01:00 | 12 | 25 | 1 | 0% | 46.97%
2024-12-25 02:00 | 12 | 25 | 2 | 0% | 43.32%
2024-12-25 03:00 | 12 | 25 | 3 | 0% | 44.36%
2024-12-25 04:00 | 12 | 25 | 4 | 0% | 45.3%
2024-12-25 05:00 | 12 | 25 | 5 | 0% | 46.43%
2024-12-25 06:00 | 12 | 25 | 6 | 0% | 47.25%
2024-12-25 07:00 | 12 | 25 | 7 | 0% | 48.19%
2024-12-25 08:00 | 12 | 25 | 8 | 0% | 47.94%
2024-12-25 09:00 | 12 | 25 | 9 | 0% | 48.31%
2024-12-25 10:00 | 12 | 25 | 10 | 1.546% | 47.75%
2024-12-25 11:00 | 12 | 25 | 11 | 6.912% | 52.33%
2024-12-25 12:00 | 12 | 25 | 12 | 3.461% | 47.17%
2024-12-25 13:00 | 12 | 25 | 13 | 3.357% | 47.92%
2024-12-25 14:00 | 12 | 25 | 14 | 1.363% | 53.77%
2024-12-25 15:00 | 12 | 25 | 15 | 0% | 49.39%
2024-12-25 16:00 | 12 | 25 | 16 | 0% | 49.91%
2024-12-25 17:00 | 12 | 25 | 17 | 0% | 50.28%
2024-12-25 18:00 | 12 | 25 | 18 | 0% | 50.85%
2024-12-25 19:00 | 12 | 25 | 19 | 0% | 50.57%
2024-12-25 20:00 | 12 | 25 | 20 | 0% | 49.98%
2024-12-25 21:00 | 12 | 25 | 21 | 0% | 49%
2024-12-25 22:00 | 12 | 25 | 22 | 0% | 47.76%
2024-12-25 23:00 | 12 | 25 | 23 | 0% | 46.84%
2024-12-26 | 12 | 26 | 0 | 0% | 47.6%
2024-12-26 01:00 | 12 | 26 | 1 | 0% | 45.63%
2024-12-26 02:00 | 12 | 26 | 2 | 0% | 44.32%
2024-12-26 03:00 | 12 | 26 | 3 | 0% | 43.2%
2024-12-26 04:00 | 12 | 26 | 4 | 0% | 41.06%
2024-12-26 05:00 | 12 | 26 | 5 | 0% | 39.82%
2024-12-26 06:00 | 12 | 26 | 6 | 0% | 38.69%
2024-12-26 07:00 | 12 | 26 | 7 | 0% | 38.09%
2024-12-26 08:00 | 12 | 26 | 8 | 0% | 37.45%
2024-12-26 09:00 | 12 | 26 | 9 | 0% | 37.59%
2024-12-26 10:00 | 12 | 26 | 10 | 0.6932% | 37.3%
2024-12-26 11:00 | 12 | 26 | 11 | 3.475% | 36.71%
2024-12-26 12:00 | 12 | 26 | 12 | 4.315% | 39.48%
2024-12-26 13:00 | 12 | 26 | 13 | 5.665% | 36.26%
2024-12-26 14:00 | 12 | 26 | 14 | 1.959% | 36.91%
2024-12-26 15:00 | 12 | 26 | 15 | 0% | 37.67%
2024-12-26 16:00 | 12 | 26 | 16 | 0% | 38.46%
2024-12-26 17:00 | 12 | 26 | 17 | 0% | 39.53%
2024-12-26 18:00 | 12 | 26 | 18 | 0% | 40.89%
2024-12-26 19:00 | 12 | 26 | 19 | 0% | 42.51%
2024-12-26 20:00 | 12 | 26 | 20 | 0% | 44.04%
2024-12-26 21:00 | 12 | 26 | 21 | 0% | 44.69%
2024-12-26 22:00 | 12 | 26 | 22 | 0% | 45.37%
2024-12-26 23:00 | 12 | 26 | 23 | 0% | 45.99%
2024-12-27 | 12 | 27 | 0 | 0% | 36.27%
2024-12-27 01:00 | 12 | 27 | 1 | 0% | 48.17%
2024-12-27 02:00 | 12 | 27 | 2 | 0% | 47.64%
2024-12-27 03:00 | 12 | 27 | 3 | 0% | 47.25%
2024-12-27 04:00 | 12 | 27 | 4 | 0% | 46.48%
2024-12-27 05:00 | 12 | 27 | 5 | 0% | 45.88%
2024-12-27 06:00 | 12 | 27 | 6 | 0% | 48.35%
2024-12-27 07:00 | 12 | 27 | 7 | 0% | 45.79%
2024-12-27 08:00 | 12 | 27 | 8 | 0% | 45.75%
2024-12-27 09:00 | 12 | 27 | 9 | 0% | 45.42%
2024-12-27 10:00 | 12 | 27 | 10 | 1.347% | 44.68%
2024-12-27 11:00 | 12 | 27 | 11 | 3.156% | 43.36%
2024-12-27 12:00 | 12 | 27 | 12 | 4.918% | 41.9%
2024-12-27 13:00 | 12 | 27 | 13 | 3.83% | 40.43%
2024-12-27 14:00 | 12 | 27 | 14 | 5.219% | 39.34%
2024-12-27 15:00 | 12 | 27 | 15 | 0% | 38.98%
2024-12-27 16:00 | 12 | 27 | 16 | 0% | 38.61%
2024-12-27 17:00 | 12 | 27 | 17 | 0% | 38.05%
2024-12-27 18:00 | 12 | 27 | 18 | 0% | 37.58%
2024-12-27 19:00 | 12 | 27 | 19 | 0% | 36.91%
2024-12-27 20:00 | 12 | 27 | 20 | 0% | 36.64%
2024-12-27 21:00 | 12 | 27 | 21 | 0% | 36.76%
2024-12-27 22:00 | 12 | 27 | 22 | 0% | 36.61%
2024-12-27 23:00 | 12 | 27 | 23 | 0% | 36.39%
2024-12-28 | 12 | 28 | 0 | 0% | 38.14%
2024-12-28 01:00 | 12 | 28 | 1 | 0% | 39.64%
2024-12-28 02:00 | 12 | 28 | 2 | 0% | 36.13%
2024-12-28 03:00 | 12 | 28 | 3 | 0% | 36.33%
2024-12-28 04:00 | 12 | 28 | 4 | 0% | 36.33%
2024-12-28 05:00 | 12 | 28 | 5 | 0% | 36.08%
2024-12-28 06:00 | 12 | 28 | 6 | 0% | 35.45%
2024-12-28 07:00 | 12 | 28 | 7 | 0% | 35.14%
2024-12-28 08:00 | 12 | 28 | 8 | 0% | 34.26%
2024-12-28 09:00 | 12 | 28 | 9 | 3.226% | 33.31%
2024-12-28 10:00 | 12 | 28 | 10 | 12.38% | 31.96%
2024-12-28 11:00 | 12 | 28 | 11 | 18.37% | 30.97%
2024-12-28 12:00 | 12 | 28 | 12 | 18.87% | 32.98%
2024-12-28 13:00 | 12 | 28 | 13 | 10.16% | 29.98%
2024-12-28 14:00 | 12 | 28 | 14 | 4.36% | 29.77%
2024-12-28 15:00 | 12 | 28 | 15 | 0% | 30.86%
2024-12-28 16:00 | 12 | 28 | 16 | 0% | 31.26%
2024-12-28 17:00 | 12 | 28 | 17 | 0% | 31.85%
2024-12-28 18:00 | 12 | 28 | 18 | 0% | 32.52%
2024-12-28 19:00 | 12 | 28 | 19 | 0% | 33.07%
2024-12-28 20:00 | 12 | 28 | 20 | 0% | 33.76%
2024-12-28 21:00 | 12 | 28 | 21 | 0% | 34.7%
2024-12-28 22:00 | 12 | 28 | 22 | 0% | 36.12%
2024-12-28 23:00 | 12 | 28 | 23 | 0% | 37.3%
2024-12-29 | 12 | 29 | 0 | 0% | 47.75%
2024-12-29 01:00 | 12 | 29 | 1 | 0% | 39.8%
2024-12-29 02:00 | 12 | 29 | 2 | 0% | 41.2%
2024-12-29 03:00 | 12 | 29 | 3 | 0% | 42.51%
2024-12-29 04:00 | 12 | 29 | 4 | 0% | 43.59%
2024-12-29 05:00 | 12 | 29 | 5 | 0% | 44.62%
2024-12-29 06:00 | 12 | 29 | 6 | 0% | 45.37%
2024-12-29 07:00 | 12 | 29 | 7 | 0% | 46.75%
2024-12-29 08:00 | 12 | 29 | 8 | 0% | 46.84%
2024-12-29 09:00 | 12 | 29 | 9 | 0% | 47.67%
2024-12-29 10:00 | 12 | 29 | 10 | 0% | 47.79%
2024-12-29 11:00 | 12 | 29 | 11 | 0% | 48.18%
2024-12-29 12:00 | 12 | 29 | 12 | 0.2442% | 48.2%
2024-12-29 13:00 | 12 | 29 | 13 | 0.5235% | 48.18%
2024-12-29 14:00 | 12 | 29 | 14 | 0.4942% | 48.4%
2024-12-29 15:00 | 12 | 29 | 15 | 0% | 49.06%
2024-12-29 16:00 | 12 | 29 | 16 | 0% | 49.38%
2024-12-29 17:00 | 12 | 29 | 17 | 0% | 49.71%
2024-12-29 18:00 | 12 | 29 | 18 | 0% | 50.03%
2024-12-29 19:00 | 12 | 29 | 19 | 0% | 54.32%
2024-12-29 20:00 | 12 | 29 | 20 | 0% | 49.89%
2024-12-29 21:00 | 12 | 29 | 21 | 0% | 49.57%
2024-12-29 22:00 | 12 | 29 | 22 | 0% | 49.23%
2024-12-29 23:00 | 12 | 29 | 23 | 0% | 49.27%
2024-12-30 | 12 | 30 | 0 | 0% | 41.02%
2024-12-30 01:00 | 12 | 30 | 1 | 0% | 47.88%
2024-12-30 02:00 | 12 | 30 | 2 | 0% | 47.87%
2024-12-30 03:00 | 12 | 30 | 3 | 0% | 47.49%
2024-12-30 04:00 | 12 | 30 | 4 | 0% | 46.69%
2024-12-30 05:00 | 12 | 30 | 5 | 0% | 46.35%
2024-12-30 06:00 | 12 | 30 | 6 | 0% | 46.75%
2024-12-30 07:00 | 12 | 30 | 7 | 0% | 46.51%
2024-12-30 08:00 | 12 | 30 | 8 | 0% | 46.4%
2024-12-30 09:00 | 12 | 30 | 9 | 0% | 45.95%
2024-12-30 10:00 | 12 | 30 | 10 | 0.7727% | 45.55%
2024-12-30 11:00 | 12 | 30 | 11 | 2.166% | 45.19%
2024-12-30 12:00 | 12 | 30 | 12 | 0.9936% | 44.7%
2024-12-30 13:00 | 12 | 30 | 13 | 2.677% | 43.48%
2024-12-30 14:00 | 12 | 30 | 14 | 2.307% | 42.73%
2024-12-30 15:00 | 12 | 30 | 15 | 0% | 42.88%
2024-12-30 16:00 | 12 | 30 | 16 | 0% | 43.33%
2024-12-30 17:00 | 12 | 30 | 17 | 0% | 43.31%
2024-12-30 18:00 | 12 | 30 | 18 | 0% | 43.78%
2024-12-30 19:00 | 12 | 30 | 19 | 0% | 43.17%
2024-12-30 20:00 | 12 | 30 | 20 | 0% | 42.8%
2024-12-30 21:00 | 12 | 30 | 21 | 0% | 45.84%
2024-12-30 22:00 | 12 | 30 | 22 | 0% | 41.98%
2024-12-30 23:00 | 12 | 30 | 23 | 0% | 41.64%
2024-12-31 | 12 | 31 | 0 | 0% | 45.21%
2024-12-31 01:00 | 12 | 31 | 1 | 0% | 41.16%
2024-12-31 02:00 | 12 | 31 | 2 | 0% | 41.31%
2024-12-31 03:00 | 12 | 31 | 3 | 0% | 44.4%
2024-12-31 04:00 | 12 | 31 | 4 | 0% | 41.78%
2024-12-31 05:00 | 12 | 31 | 5 | 0% | 42.55%
2024-12-31 06:00 | 12 | 31 | 6 | 0% | 43.62%
2024-12-31 07:00 | 12 | 31 | 7 | 0% | 44.28%
2024-12-31 08:00 | 12 | 31 | 8 | 0% | 44.22%
2024-12-31 09:00 | 12 | 31 | 9 | 0% | 44.76%
2024-12-31 10:00 | 12 | 31 | 10 | 0.3698% | 44.46%
2024-12-31 11:00 | 12 | 31 | 11 | 0.9913% | 43.84%
2024-12-31 12:00 | 12 | 31 | 12 | 0.9868% | 43.28%
2024-12-31 13:00 | 12 | 31 | 13 | 0.7549% | 42.94%
2024-12-31 14:00 | 12 | 31 | 14 | 0% | 43.15%
2024-12-31 15:00 | 12 | 31 | 15 | 0% | 48.25%
2024-12-31 16:00 | 12 | 31 | 16 | 0% | 45.47%
2024-12-31 17:00 | 12 | 31 | 17 | 0% | 46.62%
2024-12-31 18:00 | 12 | 31 | 18 | 0% | 47.49%
2024-12-31 19:00 | 12 | 31 | 19 | 0% | 48.19%
2024-12-31 20:00 | 12 | 31 | 20 | 0% | 48.48%
2024-12-31 21:00 | 12 | 31 | 21 | 0% | 48.4%
2024-12-31 22:00 | 12 | 31 | 22 | 0% | 47.38%
2024-12-31 23:00 | 12 | 31 | 23 | 0% | 46.41%

## Monthly
Month | Month Name | Hours | Solar CF | Wind CF | Solar (MWh) | Wind (MWh) | Total (MWh) | Deficit Hours | Deficit (MWh) | Surplus (MWh) | Max Deficit (MW) | Max SoC (MWh) | Min SoC (MWh)
1 | Jan
2 | Feb
3 | Mar
4 | Apr
5 | May
6 | Jun
7 | Jul
8 | Aug
9 | Sep
10 | Oct
11 | Nov
12 | Dec
TOTAL

## Key Insights
BASELOAD PPA KEY INSIGHTS
1. NON-LINEAR BATTERY SCALING
Battery requirements scale exponentially with baseload percentage:
- 50% baseload: ~1 MWh battery
- 80% baseload: ~8 MWh battery
- 100% baseload: ~109 MWh battery
Implication: Target 80% for best cost/delivery balance
2. SUMMER NIGHTS ARE THE BOTTLENECK
Critical periods are July-August nights, not winter:
- Weaker summer winds (reduced pressure gradients)
- Anticyclones can persist for days
- Solar contributes nothing at night
3. 10% PASS REDUCES BATTERY 50-100%
Allowing 10% non-delivery (878 hrs/yr) saves dramatically:
- 50% baseload: 1 MWh -> 0 MWh (-100%)
- 80% baseload: 8 MWh -> 3 MWh (-60%)
- 100% baseload: 109 MWh -> 57 MWh (-48%)
4. OPTIMAL SOLAR/WIND RATIO = 1:1
For SE3, equal MW of solar and wind provides best complementarity
- Solar: Summer daytime (CF ~11.5%)
- Wind: Year-round, better at night (CF ~30%)
5. BATTERY DURATION REQUIREMENT
80% baseload requires ~24h battery duration:
- 8 MWh / 0.33 MW = 24 hours
- Typical Li-ion: 2-4h (would need oversizing or flow battery)
6. RECOMMENDED PPA STRUCTURE
80% baseload + 10% pass allowance + spot settlement for surplus
- Reasonable battery requirement (~3 MWh)
- Balanced risk between buyer/seller
- Monetize surplus production on spot market

## Sensitivity
BATTERY REQUIREMENT SENSITIVITY
Baseload % | Baseload (MW) | Deficit Hours | Deficit % | Battery (MWh) | Duration (days)
50% | 0.208 | 447 | 5% | 1 | 0.6
60% | 0.249 | 1153 | 13% | 3 | 0.9
70% | 0.291 | 2186 | 25% | 5 | 1.1
80% | 0.332 | 3319 | 38% | 8 | 1.6
90% | 0.374 | 4560 | 52% | 17 | 2.8
100% | 0.415 | 5671 | 65% | 109 | 15.5