## Slide 1
Baseload PPA Analysis
Solar + Wind + Battery Energy Storage
SE3 Sweden | 2024 Analysis | 1 MW Solar + 1 MW Wind

## Slide 2
Executive Summary
Key Findings
100% baseload is impractical - requires 109 MWh battery (seasonal storage)
80% baseload is the sweet spot - only 8 MWh battery needed
Summer nights are critical - not winter as commonly assumed
20.8%
Combined Capacity Factor
8 MWh
Battery for 80% Baseload
13x
More Battery for 100% vs 80%

## Slide 3
The Challenge: Baseload PPA
What is Baseload PPA?
A Power Purchase Agreement that guarantees constant power delivery 24/7/365, regardless of weather conditions.
Unlike pay-as-produced contracts, the seller bears all volume risk.
The Problem
• Solar only produces during daytime • Wind varies unpredictably • Combined output still fluctuates • Gaps must be filled somehow
Analysis Question
How large a battery is needed to guarantee baseload delivery from solar + wind?
Our Approach
• 1 MW solar (PVsyst profile) • 1 MW wind (ENTSO-E actual data) • Hourly simulation for full year • Calculate max cumulative deficit • Test different baseload levels

## Slide 4
Methodology
Data Sources
Solar Profile
PVsyst simulation
south_lundby.csv
CF: 11.5%
Wind Profile
ENTSO-E actual
SE3 2024 normalized
CF: 30.0%
Time Period
Full year 2024
8,784 hours
Hourly resolution
Battery Sizing Algorithm
Max Drawdown Method:
deficit[t] = max(0, baseload - production[t])
cumsum[t] = cumsum[t-1] + (production[t] - baseload)
battery_size = max(peak_cumsum - cumsum[t]) for all t
Solar Installed
1.0 MW
Wind Installed
1.0 MW
Mean Production
0.415 MW
Annual Output
3,647 MWh

## Slide 5
Results: Battery Sizing vs Baseload Level
Non-Linear Scaling of Battery Requirements
Baseload % | Baseload (MW) | Deficit Hours | Deficit % | Battery (MWh) | Duration
50% | 0.208 | 447 | 5% | 1 | 14 hours
60% | 0.249 | 1,153 | 13% | 3 | 22 hours
80% | 0.332 | 3,319 | 38% | 8 | 1.6 days
90% | 0.374 | 4,560 | 52% | 17 | 2.8 days
100% | 0.415 | 5,671 | 65% | 109 | 15.5 days
Key Insight: Going from 80% to 100% baseload increases battery need by 13x (8 → 109 MWh)

## Slide 6
Key Insight: Summer Nights Are the Bottleneck
Counter-Intuitive Finding
The most challenging periods are summer nights (July-August), NOT winter darkness!
Why Summer Nights?
• Weaker summer winds - reduced pressure gradients • Anticyclones persist - high pressure for days • Solar = zero at night - regardless of season • Dunkelflaute - extended low wind + no sun
Critical Periods
• 50% baseload: July 23-24 (16 hours) • 80% baseload: Nov 6-9 (69 hours) • 100% baseload: Multiple weeks
Pass Hours by Month (10% worst)
July
27%
August
20%
June
17%
September
12%
May
10%
October
8%
January
1%

## Slide 7
Key Insight: 10% Pass Reduces Battery 50-100%
Effect of Allowing Non-Delivery Hours
If the PPA allows 10% non-delivery (878 hours/year), battery requirements drop dramatically:
Baseload Level | 100% Delivery | 90% Delivery | Battery Reduction
50% (0.208 MW) | 1.2 MWh | 0 MWh | -100%
80% (0.332 MW) | 8.2 MWh | 3.3 MWh | -60%
100% (0.415 MW) | 109 MWh | 57 MWh | -48%
Implication: The worst 10% of hours drive most of the battery requirement. Small contractual flexibility yields outsized savings.
Recommendation: Negotiate for pass hours in PPA contracts - even small allowances save significant capital.

## Slide 8
Recommendations
Key Takeaways
Target 80% Baseload
Best balance between delivery guarantee and capital cost. 8 MWh battery vs 109 MWh for 100%.
Negotiate Pass Hours
10% pass allowance reduces battery by 50-100%. Focus on summer night flexibility.
1:1 Solar/Wind Ratio
Optimal complementarity for SE3. Solar covers days, wind covers nights/winter.
Recommended PPA Structure
PPA Type | Battery Need | Risk Allocation | Premium
Pay-as-produced | 0 MWh | Buyer takes volume risk | Low
80% baseload + 10% pass | ~3 MWh | Balanced risk | Medium
100% baseload | 109 MWh | Seller takes all risk | Very High

## Slide 9
Appendix: Data Sources and Parameters
Data Sources
Solar Production Profile
PVsyst simulation - south_lundby.csv
South-facing fixed tilt, SE3 irradiance
Wind Production Profile
ENTSO-E Transparency Platform
SE3 actual generation 2024, normalized
Electricity Prices
elprisetjustnu.se API
SE3 hourly spot prices
Analysis Period
Full year 2024 (leap year)
8,784 hours, hourly resolution
Key Parameters
Solar Installed | 1.0 MW
Wind Installed | 1.0 MW
Solar Capacity Factor | 11.5%
Wind Capacity Factor | 30.0%
Combined Capacity Factor | 20.8%
Mean Production | 0.415 MW
Annual Production | 3,647 MWh
BESS Round-trip Efficiency | 90%
Analysis Files
elpris/baseload_analysis.py
data/reports/baseload_ppa_analysis.xlsx
data/reports/insights/baseload_ppa_key_insights.md